## Info
Revision date 12-08-2026
Quick overview
The most common used parameters.
Modbus Info
General information about modbus RTU/TCP-IP
Modbus RTU Connection
How to connect Modbus RTU (RS-485)
BACnet Info
General information about BACnet TCP-IP
BACnet Connection
How to connect BACnet TCP-IP
Parameters
Complete list of all modbus and BACnet parameters.
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ AirTM Plus
Modbus and BACnet protocol
Software version 1.09

## BTL_certificate
Actual BACnet certificate can be found on OJ Electronics A/S homepage
OJ AIR™ PLUS MASTER: Advanced AHU Control System ¦ OJ Electronics
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Quick overview
BACnet / Modbus overview
|  |  |  | BACnet | Modbus
|  |  | Actual exhaust temp. [1/100°C] | AI 22 | 3x0026
|  |  | Actual extract flow [l/s] | AI 7 | 3x0009
|  |  | Extract motor output percentage [1/100%] | AI 30 | 3x0036
|  |  | Setpoint for extract flow, low speed [l/s] | AV 59 | 4x0069
|  |  | Setpoint for extract flow, medium speed [l/s] | AV 60 | 4x0070
|  |  | Setpoint for extract flow, high speed [l/s] | AV 61 | 4x0071
|  |  | Rot. heat exchanger – output percent. [%] | AI 73 | 3x0097
|  |  | Actual outdoor temp. [1/100°C] | AI 20 | 3x0024
|  |  | Outdoor Air filter pressure [Pa] | AI 27 | 3x0031
|  |  | Supply Air filter monitor max. alarm limit [Pa] | AI 31 | 3x0039
|  |  | Extract Air filter pressure [Pa] | AI 28 | 3x0032
|  |  | Max. alarm limit, extract filter pressure drop [Pa] | AI 32 | 3x0048
|  |  | Actual supply air flow [l/s] | AI 5 | 3x0007
|  |  | Supply motor output percentage [1/100%] | AI 29 | 3x0034
|  |  | Setpoint for supply air flow, low speed [l/s] | AV 56 | 4x0011
|  |  | Setpoint for supply air flow, medium speed [l/s] | AV 57 | 4x0320
|  |  | Setpoint for supply air flow, high speed [l/s] | AV 58 | 4x0012
|  |  | Actual room temperature [1/100 °C] | AI 21 | 3x0025
|  |  | Actual extract duct pressure [Pa] | AI 3 | 3x0005
| BACnet | Modbus | Setpoint for duct pressure, extract, low speed [Pa] | AV 53 | 4x0063
|  |  | Setpoint for duct pressure, extract, medium speed [Pa] | AV 54 | 4x0064
Extended low speed –> Active | BI 3 | 1x0004 | Setpoint for duct pressure, extract, high speed [Pa] | AV 55 | 4x0065
Extended high speed –> Active | BI 4 | 1x0005
Alarm relay 1 (A-alarm) | BI 30 | 1x0035 | Actual supply Air temperature [1/100°C] | AI 16 | 3x0020
Alarm relay 2 (B-alarm) | BI 31 | 1x0036 | Temperature Control type setting | AV 133 | 4x0148
Alarm reset signal (AutoReturn to zero) | BV 0 | 0x0001 | Temperature setpoint for actual control type | AV 134 | 4x0149
|  |  | Min. limit, supply air temp. [1/100°C] | AV 135 | 4x0150
|  |  | Max. limit, supply air temp. [1/100°C] | AV 136 | 4x0151
|  |  | Actual heating 1 power [1/100%] | AI 36 | 3x0054
|  |  | Heating relay 1, active | BI 26 | 1x0031
AI = Analog Input |  |  | Actual Heat 1, RWT [1/100°C] | AI 26 | 3x0030
AV = Analog Value |  |  | Actual cooling power [1/100%] | AI 38 | 3x0056
BI = Binary Input |  |  | Actual supply air duct pressure [Pa] | AI 1 | 3x0003
BV = Binary Value |  |  | Setpoint for duct pressure, supply air, low speed [Pa] | AV 50 | 4x0003
|  |  | Setpoint for duct pressure, supply air, medium speed [Pa] | AV 51 | 4x0322
|  |  | Setpoint for duct pressure, supply air, high speed [Pa] | AV 52 | 4x0004
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
1
3
2
4
5
6
7

## Modbus info
Modbus RTU/TCP
OJ AirTM Plus, Program version 1.00 and later versions
Overview
This Protocol contains all Modbus addresses and registers in the OJ AirTM Plus
Updating of values in the individual registers is dependent on the actual configuration
of the air handling unit. It will, for example, be possible to read out water heating coil
temperature register 3x0030 irrespective of whether or not an water heating coil
is installed in the system concerned.
The value will, however, only be used if the associated temperature sensor is installed.
Modbus can access single addresses or several addresses simultaneously,
either reading or writing 1-bit or 16-bit values.
A Modbus address contains either a 1-bit value or a 16-bit integer.
Communication
TCP/IP................................................................. 10/100 Mbit shielded RJ45 port
HMI port...................................... Modbus RS485, 115kbaud, 120Ω termination
BMS port .................... Modbus RS485, max. 38.4kbaud, No 120Ω termination
Modbus port A...........................................RS485, 38.4kbaud, 120Ω termination
Modbus port B1, B2..................................RS485, 38.4kbaud, 120Ω termination
Modbus data format
Modbus data types are 1-bit values and 16-bit values.
Modbus Type |  | Description | Reference
Coil Status (R/W) |  | Discrete Output | 0x
Input Status (R) |  | Discrete Input | 1x
Holding Register (R/W) |  | 16-bit Output Register | 4x
Input register (R) |  | 16-bit Input Register | 3x
R = Read Only
R/W = Read / Write
Supported Modbus commands
OJ AirTM Plus supports the following Modbus commands:
Function code | Description
1 | Read Coil Status
2 | Read Input Status
3 | Read Holding Registers
4 | Read Input Registers
5 | Force Single Coil
6 | Preset Single Registers
8 | Diagnostics. Sub-function 00 Only - Return Query Data (loop back)
15 | Force Multiple Coils
16 | Preset Multiple Registers
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Modbus RTU Connection
Modbus RTU connection
Internal system communication ports (RJ12) | Cable for BMS Modbus Connection (RJ12)
Note: Remember RS485 converter tool.
External system communication port (RJ12) | Cable for BMS TCP/IP connection (RJ45)
Connector pin out for Modbus cable (RJ12) | How to correctly mount connectors in a Modbus cable (RJ12)
Cable for BMS connection (RJ12)
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## BacNet info
BACnet
OJ AirTM Plus , Program version 1.00 and subsequent versions.
Overview
BACnet features enable BACnet control and monitoring of a complete Air Handling Unit (AHU), which is equipped with an OJ-AirTM Plus controller.
The BACnet functionality is implemented in OJ-AirTM Plus with software version 1.xx or higher.
This protocol contains all BACnet addresses and registers in the OJ-AirTM Plus. Updating of values in the individual registers is dependent on
the actual configuration of the air handling unit. It will, for example, be possible to read out water heating coil temperature Analog Input
Object Instance 26 irrespective of whether or not an water heating coil is installed in the system concerned.
The value will, however, only be used if the associated temperature sensor is installed. The OJ-AirTM Plus is a BACnet Advanced Application
Controller (B-AAC) Supported Data Link Layer Options: BACnet IP Please also see the documents "OJ-AirTM Plus BACnet PICS"
(Protocol Implementation Conformance Statement) and "OJ-AirTM Plus EDE" (Engineering Data Exchange).
Communication
BACnet TCP/IP: 1 pcs. 10/100Mbit Ethernet, RJ45 socket
Standard BACnet TCP/IP communication port: 47808
Object Indentifier:
The Object_Identifier is automatic set to the last 5 digits in the OJ AirTM Plus IP adress.
Samples: | IP-adresse = 172.21.0.95 ………………..…….. Object Identifier = 95
IP-adresse = 155.37.0.216 ………………....... Object Identifier = 216
IP-adresse = 155.37.35.123 ………………..... Object Identifier = 35123
IP-adresse = 132.65.124.103 ……………….. Object Identifier = 24103
IP-adresse = 172.20.211.47 ………………..... Object Identifier = 11047
IP-adresse = 155.37.111.123 ………………... Object Identifier = 11123
IP-adresse = 168.25.111.1 ………………..….. Object Identifier = 11001
OBS! The Object_Identifier will only be set once and only when the OJ-AirTM Plus is powered up or restarted
Max. 300 values ​​can at the same time be registered to the COV (Change Of Value)
BACnet Interoperability Building Blocks Supported
Data Sharing |  | DS-RP-B | Data Sharing-Read Property-B
Data sharing |  | DS-WP-B | Data Sharing-Write Property-B
Device Management |  | DM-DDB-B | Device Management-Dynamic Device Binding-B
Device Management |  | DM-DOB-B | Device Management-Dynamic Object Binding-B
Device Management |  | DM-DCC-B | Device Management-Dynamic Communication Control-B
Standard Object Types Supported
Object type | Properties
Analog Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, Reliability, COV_Increment
Analog Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment.
Binary Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Polarity.
Binary Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Priority_Array, Relinquish_Default.
Device | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Aplication_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_list, Max_APDU_Length_Accepted, Segmentation_Supported, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision.
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## BacNet Connection
BacNet connection
Cable for BMS TCP/IP connection / BacNet connection (RJ45)
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S

## Parameter
| Component | Function | Standard/ Special | Name | SI Unit | Modbus register | SW vers. | BacNet parameter | SW vers. | Min | Max | Factory settings | Comments in English
| Component | Function | Standard/ Special | Name | SI Unit | Coil status (R/W) (0x) | SW vers. | Binary value (R/W) (BV) | SW vers. | Min | Max | Factory settings | Comments in English
0x0E00 | AHU Controller | Alarm | Standard | Alr_Reset_USet |  | 0x0001 | 1.01 | BV0 | 1.01 | 0 | 1 |  | Reset Alarms (AutoReturn to zero)
0x0002 | Heat Exchanger | Cooling recovery | Standard | AHU_CoolRecovFunc |  | 0x0002 | 1.01 | BV1 | 1.01 | 0 | 1 | 0 | Cooling Recovery: ON/OFF
0x0370 | AHU Controller | Summer Night Cooling | Standard | SNC_Func |  | 0x0003 | 1.01 | BV2 | 1.01 | 0 | 1 | 0 | Summer Night Cooling: ON/OFF
0x0380 | AHU Controller | Summer/Winter comp. | Standard | SWTC_Func |  | 0x0004 | 1.01 | BV3 | 1.01 | 0 | 1 | 0 | Summer/winter temperature compensation: ON/OFF
0x03C0 | Fan | Outdoor temp. comp. | Standard | AR_FlwTmpCmpFunc |  | 0x0005 | 1.01 | BV4 | 1.01 | 0 | 1 | 0 | Air Flow: Outdoor Air Temperature Compensation ON/OFF
0x03E0 | Recirculation | Recirculation heat | Standard | MODREC_Func_On |  | 0x0006 | 1.01 | BV5 | 1.01 | 0 | 1 | 0 | Recirculation: ON/OFF ("1" = Open damper)
0x0420 | Fan | Speed | Standard | CL_Cool_FlwForceFc |  | 0x0007 | 1.01 | BV6 | 1.01 | 0 | 1 | 0 | Air Flow: Fan Speed Increased when Active Cooling: ON/OFF
0x0800 | AHU Controller | Summer/winter time | Standard | SWTC_SumFunc |  | 0x0008 | 1.01 | BV7 | 1.01 | 0 | 1 | 1 | Automatic Summer/winter time: ON/OFF
0x0810 | Fan | Speed | Standard | ExtDrfHiPeriod |  | 0x0009 | 1.01 | BV8 | 1.01 | 0 | 1 | 0 | High Speed: Active.
0x0811 | Fan | Speed | Standard | ExtDrfPeriodON |  | 0x0010 | 1.01 | BV9 | 1.01 | 0 | 1 | 0 | High Speed: Run-on time active
0x0008 | Heat Exchanger | Rotation CCW | Standard | EXC_CCV |  | 0x0011 | 1.01 | BV26 | 1.01 | 0 | 1 | 0 | Rotary Heat Exchanger, Counter clock wise (CCW) Rotation.
| AHU controller | Control | Standard | ExtDrfMePeriod |  | 0x0012 | 1.01 | BV30 | 1.01 | 0 | 1 | 0 | Input for forced medium speed active
| AHU Controller | Summer Night Cooling | Standard | SNC_FuncLoSpeed |  | 0x0013 | 1.01 | BV27 | 1.01 | 0 | 1 | 0 | Summer Night Cooling activated in low speed
| AHU Controller | Speed | Standard | ExtHighSpdSet |  | 0x0014 | 1.01 | BV28 | 1.01 | 0 | 1 | 0 | High Speed: Digital input active.
| El-Heater Coil 1 | Flow limit | Standard | EL_HT1_LimitStep_1Uset |  | 0x0015 | 1.10 | BV31 | 1.10 | 0 | 1 | 0 | El-Heater Coil 1: Use min. and max. Supply Air Flow setting on El-Heater step 1.
| El-Heater Coil 2 | Flow limit | Standard | EL_HT2_LimitStep_1Uset |  | 0x0016 | 1.10 | BV32 | 1.10 | 0 | 1 | 0 | El-Heater Coil 2: Use min. and max. Supply Air Flow setting on El-Heater step 1.
| El-Heater Preheater Coil | Flow limit | Standard | PH_EL_LimitStep_1Uset |  | 0x0017 | 1.10 | BV33 | 1.10 | 0 | 1 | 0 | El Pre-Heater Coil: Use min. and max. Supply Air Flow setting on El-Heater step 1.
0x0000 | Pressure | Calibration | Standard | ManZeroCali |  | 0x0020 | 1.01 | BV10 | 1.01 | 0 | 1 | 0 | Pressure Transmitters: Start Manual Zero Calibration (can be used together with automatic zero calibration) Is automatically reset to zero (OFF) once calibration has been completed
0x0001 | Pressure | Calibration | Standard | AutoZeroCali |  | 0x0021 | 1.01 | BV11 | 1.01 | 0 | 1 | 0 | Pressure Transmitters: Automatic Zero Calibration: ON/OFF
0x0390 | Filter | Alarm | Standard | FiltDynAlrFunc |  | 0x0022 | 1.01 | BV12 | 1.01 | 0 | 1 | 0 | Filter alarms: Dynamic ON/OFF OFF = Static Pressure drop Alarm limit (constant) ON = Dynamic Pressure drop Alarm limit (limit based on Air Flow)
0x0391 | Filter | Calibration | Standard | FiltCalibrate |  | 0x0023 | 1.01 | BV13 | 1.01 | 0 | 1 | 0 | Filter alarms: Start filter calibration. Is automatically reset to zero (OFF) once calibration has been completed. NOTE! ONLY IF "DYNAMIC MODE" IS SET
0x0436 | Combi Coil | Control | Standard | CmbEnCtrlMB |  | 0x0025 | 1.01 | BV21 | 1.01 | 0 | 1 | 0 | Combi Coill: Enable control via external Modbus [1=Modbus/0=Dig. input]
0x0437 | Combi Coil | Control | Standard | CmbEnHeatMB |  | 0x0026 | 1.01 | BV17 | 1.01 | 0 | 1 | 1 | Combi Coil: Hot water supply is available.
0x0438 | Combi Coil | Control | Standard | CmbEnCoolMB |  | 0x0027 | 1.01 | BV18 | 1.01 | 0 | 1 | 1 | Combi Coil: Cold water supply is available.
0x0095 | Temperature | Outdoor temp. | Standard | TR_MBT_OA_Act |  | 0x0028 | 1.01 | BV15 | 1.01 | 0 | 1 | 0 | Outdoor temperature: Use Readings from BMS.
0x0096 | Temperature | Room temp. | Standard | TR_MBT_Room1Activ |  | 0x0029 | 1.01 | BV16 | 1.01 | 0 | 1 | 0 | Room temperature: Use Readings from BMS.
0x0410 | Recirculation | Recirculation heat | Standard | ExtMB_ForceRecirc |  | 0x0030 | 1.01 | BV19 | 1.01 | 0 | 1 | 0 | Recirculation: Force recirculation by Ext. Modbus ("1" = Open damper)
0x0411 | Recirculation | Recirculation heat | Standard | ExtMBEnbl_ForceRec |  | 0x0031 | 1.01 | BV20 | 1.01 | 0 | 1 | 0 | Recirculation: Enable Force recirculation signal from Ext. Modbus.
| Filter | Outdoor Air | Standard | Filt_DynAlrFunc_OA |  | 0x0032 | 1.01 | BV22 | 1.01 | 0 | 1 | 0 | Outdoor Air Filter (OA): Dynamic Alarm function ON/OFF. OFF = Static Alarm Limit (Constant). ON = Dynamic Alarm Limit (Limit based on flow)
| Filter | Supply Air | Standard | Filt_DynAlrFunc_SA |  | 0x0033 | 1.01 | BV23 | 1.01 | 0 | 1 | 0 | Supply Air Filter (SA): Dynamic Alarm function ON/OFF. OFF = Static AlarmLimit (Constant). ON = Dynamic AlarmLimit (Limit based on flow)
| Filter | Extract Air | Standard | Filt_DynAlrFunc_EA1 |  | 0x0034 | 1.01 | BV24 | 1.01 | 0 | 1 | 0 | Extract Air Filter 1 (EX): Dynamic Alarm function ON/OFF. OFF = Static AlarmLimit (Constant). ON = Dynamic AlarmLimit (Limit based on flow)
| Filter | Extract Air | Standard | Filt_DynAlrFunc_EA2 |  | 0x0035 | 1.01 | BV25 | 1.01 | 0 | 1 | 0 | Extract Air Filter 2 (EX): Dynamic Alarm function ON/OFF. OFF = Static AlarmLimit (Constant). ON = Dynamic AlarmLimit (Limit based on flow)
| Compressor | Drive | Standard | MNT_DV_Compressor |  | 0x0040 | 1.01 | BV29 | 1.01 | 0 | 1 |  | Drive Compressor: installed
| AHU controller | Control | Standard | ExtDrfMePeriod |  | 0x0812 | 1.01 | BV30 | 1.01 | 1 | 0 |  | Input for forced medium speed active
| Component | Function | Standard/ Special | Name | SI Unit | Input status (R) (1x) | SW vers. | Binary Input (R) (BI) | SW vers. | Min | Max | Factory settings | Comments in English
| AHU Controller | Status | Standard | Operation |  | 1x0001 | 1.01 | BI0 | 1.01 | 0 | 1 |  | Operation ON/OFF
0x1001 | AHU Controller | Speed | Standard | ExtStop |  | 1x0002 | 1.01 | BI1 | 1.01 | 0 | 1 |  | External Stop: Active
0x1002 | AHU Controller | Speed | Standard | ExtHiSpeed |  | 1x0003 | 1.01 | BI2 | 1.01 | 0 | 1 |  | External High Speed: Active
0x1810 | AHU Controller | Speed | Standard | ExtDrfLoSpeed |  | 1x0004 | 1.01 | BI3 | 1.01 | 0 | 1 |  | Extended Low Speed: Active
0x1811 | AHU Controller | Speed | Standard | ExtDrfHiSpeed |  | 1x0005 | 1.01 | BI4 | 1.01 | 0 | 1 |  | Boost speed: Active
0x1013 | AHU Controller | Fire | Standard | ExtBrandStop |  | 1x0006 | 1.01 | BI78 | 1.01 | 0 | 1 |  | Fire Stop input: Active
0x1812 | AHU Controller | Speed | Standard | ExtDrfMeSpeed |  | 1x0007 | 1.01 | BI225 | 1.01 | 0 | 1 |  | Extended Medium Speed: Active
0x1341 | Heating Coil 1 | Status | Standard | El_HT1_BattPowerRed |  | 1x0010 | 1.01 | BI5 | 1.01 | 0 | 1 |  | Electric Heating Coil 1: Power to Electric Heating Coil reduced due to low flow
0x1370 | AHU Controller | Summer Night Cooling | Standard | SNC_Drift |  | 1x0011 | 1.01 | BI6 | 1.01 | 0 | 1 |  | Summer Night cooling: Active
0x1371 | AHU Controller | Summer Night Cooling | Standard | SNC_Reset |  | 1x0012 | 1.01 | BI7 | 1.01 | 0 | 1 |  | Summer Night Cooling: Reset of Heating Count up: Active.
0x1380 | AHU Controller | Summer/Winter comp. | Standard | SWTC_WintComp |  | 1x0013 | 1.01 | BI8 | 1.01 | 0 | 1 |  | Winter temperature compensation: Active
0x1381 | AHU Controller | Summer/Winter comp. | Standard | SWTC_SumComp |  | 1x0014 | 1.01 | BI9 | 1.01 | 0 | 1 |  | Summer temperature compensation: Active
0x13D0 | AHU Controller | Summer/Winter comp. | Standard | SWTC_SumFunc |  | 1x0015 | 1.01 | BI10 | 1.01 | 0 | 1 |  | Summer/winter actual status. OFF = winter operation ("0") ON = summer operation ("1")
0x13E1 | Recirculation | Recirculation heat | Standard | MODREC_Status |  | 1x0016 | 1.01 | BI11 | 1.01 | 0 | 1 |  | Recirculation status ("1" = Open Recirculation damper)
0x100D | Heat Exchanger | Status | Standard | EXC_Exercise |  | 1x0017 | 1.01 | BI12 | 1.01 | 0 | 1 |  | Heat Exchanger Exercise: Active
0x1321 | Heat Exchanger | Status | Standard | CExcIceProtect |  | 1x0018 | 1.01 | BI13 | 1.01 | 0 | 1 |  | Cross-flow exchanger: Reduced Power (Ice Protection Active)
0x1103 | Fan | Status | Standard | AR_SA_DuctMinFlow |  | 1x0019 | 1.01 | BI14 | 1.01 | 0 | 1 |  | Supply duct pressure controller min. flow: Active
0x1104 | Fan | Status | Standard | AR_SA_DuctMaxFlow |  | 1x0020 | 1.01 | BI15 | 1.01 | 0 | 1 |  | Supply duct pressure controller max. flow: Active
0x1203 | Fan | Status | Standard | AR_EA_DuctMinFlow |  | 1x0021 | 1.01 | BI16 | 1.01 | 0 | 1 |  | Extract duct pressure controller min. flow: Active
0x1204 | Fan | Status | Standard | AR_EA_DuctMaxFlow |  | 1x0022 | 1.01 | BI17 | 1.01 | 0 | 1 |  | Extract duct pressure controller max. flow: Active
0x1003 | Heat Exchanger | Status | Standard | CoolRecovery |  | 1x0023 | 1.01 | BI18 | 1.01 | 0 | 1 |  | Cooling recovery: Active
0x1332 | Heating Coil 1, Water | Status | Standard | HW1FrostReg |  | 1x0024 | 1.01 | BI19 | 1.01 | 0 | 1 |  | Water Heating Coil 1: Frost protection: Active
0x1333 | Heating Coil 1, Water | Status | Standard | HW1PumpExer |  | 1x0025 | 1.01 | BI20 | 1.01 | 0 | 1 |  | Water Heating Coil 1: Circulation Pump Exercise: Active
0x1350 | Cooling Coil, water | Status | Standard | CL_CW_PumpExer |  | 1x0026 | 1.01 | BI21 | 1.01 |  |  |  | Water Cooling Coil: Pump Exercise: Active
0x1402 | Heating Coil 1, Electric | Status | Standard | Heat_FlwDnReg |  | 1x0027 | 1.01 | BI22 | 1.01 | 0 | 1 |  | El-Heating Coil: Reduced Power (insufficient flow): Active
0x1460 | AHU Controller | Temperature | Standard | TempRegMinSup |  | 1x0028 | 1.01 | BI23 | 1.01 | 0 | 1 |  | Min. Supply Air Temperature Limit control: Active. (Only if Room or Extract Air temp. control.)
0x1461 | AHU Controller | Temperature | Standard | TempRegMaxSup |  | 1x0029 | 1.01 | BI24 | 1.01 | 0 | 1 |  | Max. Supply Air Temperature Limit control: Active. (Only if Room or Extract Air temp. control.)
0x1922 | Heat Exchanger | Status | Standard | BattEXC_Exer |  | 1x0030 | 1.01 | BI25 | 1.01 | 0 | 1 |  | Run Around Coil: Pump Exercise: Active
0x1400 | Heating Coil 1 | Status | Standard | Heat_RE1_DO1 |  | 1x0031 | 1.01 | BI26 | 1.01 | 0 | 1 |  | Heating Coil 1 Relay 1: Active.
0x1420 | Cooling Coil | Status | Standard | Cool_RE1 |  | 1x0032 | 1.01 | BI27 | 1.01 | 0 | 1 |  | Cooling Coil Relay 1: Active.
0x1921 | Heat Exchanger | Status | Standard | BattEXC_PumpRE |  | 1x0033 | 1.01 | BI28 | 1.01 | 0 | 1 |  | Run Around Coil: Circulation Pump: Active
0x100E | AHU Controller | Alarm | Standard | AlrActive |  | 1x0034 | 1.01 | BI29 | 1.01 | 0 | 1 |  | At least one Alarm: Active.
0x1480 | AHU Controller | Alarm | Standard | Alr_RE1 |  | 1x0035 | 1.01 | BI30 | 1.01 | 0 | 1 |  | Alarm Relay 1 (A-alarm): Active
0x1481 | AHU Controller | Alarm | Standard | Alr_RE2 |  | 1x0036 | 1.01 | BI31 | 1.01 | 0 | 1 |  | Alarm Relay 2 (B-alarm): Active
0x1488 | AHU Controller | Fire | Standard | Alr_FireSignal |  | 1x0037 | 1.01 | BI32 | 1.01 | 0 | 1 |  | Fire Alarm Signal (room sensor): Active
0x1489 | AHU Controller | Smoke | Standard | Alr_SmokeSig |  | 1x0038 | 1.01 | BI33 | 1.01 | 0 | 1 |  | Smoke Evacuation: Active
0x1485 | Heating Coil, Electric | Alarm | Standard | EL1_OverHtBac |  | 1x0039 | 1.01 | BI219 | 1.01 | 0 | 1 |  | Electric Heating Coil: High temperature alarm: Active
0x1E3D | Heating Coil, Electric | Alarm | Standard | AlrElBattCont |  | 1x0040 | 1.01 | BI220 | 1.01 | 0 | 1 |  | Electric Heating Coil: Relay stuck: Active
0x1390 | Filter | Supply Air | Standard | FiltSupAlarm |  | 1x0041 | 1.01 | BI35 | 1.01 | 0 | 1 |  | Supply Air Filter: Filter Alarm: Active. (Pressure drop above set limit)
0x1391 | Filter | Extract Air | Standard | FiltExtAlarm |  | 1x0042 | 1.01 | BI36 | 1.01 | 0 | 1 |  | Extract Air Filter: Filter Alarm: Active. (Pressure drop above set limit)
0x1322 | Heat Exchanger | De-icing | Special | CExcDeIcing |  | 1x0043 | 1.01 | BI297 | 1.01 | 0 | 1 |  | Cross-Flow Heat Exchanger Power reduction due to de-icing; Active.
0x13B1 | Heating Coil 2, Electric | Status | Standard | ElBat2PowerRed |  | 1x0045 | 1.01 | BI298 | 1.01 | 0 | 1 |  | El-Heating Coil 2: Reduced Power (insufficient flow): Active
0x1394 | Filter | Alarm | Standard | FiltSup2Alarm |  | 1x0048 | 1.01 | BI253 | 1.01 | 0 | 1 |  | Supply Air Filter 2: Filter Alarm: Active. (Pressure above Limit)
0x1395 | Filter | Alarm | Standard | FiltExt2Alarm |  | 1x0049 | 1.01 | BI254 | 1.01 | 0 | 1 |  | Extract Air Filter 2: Filter Alarm: Active (Pressure above Limit)
0x1100 | Temp. Supply | Alarm | Standard | SupTempSensErr |  | 1x0050 | 1.01 | BI37 | 1.01 | 0 | 1 |  | Supply Air Temperature: Sensor Alarm: Active
0x1200 | Temp. Extract | Alarm | Standard | ExtTempSensErr |  | 1x0051 | 1.01 | BI38 | 1.01 | 0 | 1 |  | Extract Air Temperature: Sensor Alarm: Active
0x1300 | Temp. Out door | Alarm | Standard | OutDoorSensErr |  | 1x0052 | 1.01 | BI39 | 1.01 | 0 | 1 |  | Outdoor Air Temperature: Sensor Alarm: Active
0x1310 | Temp. Room | Alarm | Standard | RoomSensErr |  | 1x0053 | 1.01 | BI40 | 1.01 | 0 | 1 |  | Room Temperature: Sensor Alarm: Active
0x1320 | Temp. Exhaust | Alarm | Standard | ExhaustSensErr |  | 1x0054 | 1.01 | BI41 | 1.01 | 0 | 1 |  | Exhaust Air Temperature: Sensor Alarm: Active
0x1330 | Heating coil 1, Water | Alarm | Standard | HW1SensErr |  | 1x0055 | 1.01 | BI42 | 1.01 | 0 | 1 |  | Heating Coil Return Water Temperature: Sensor Alarm: Active
0x1920 | Heat Exchanger | Alarm | Standard | BattEXC_SensEr |  | 1x0056 | 1.01 | BI43 | 1.01 | 0 | 1 |  | Run Around Coil Water Temperature: Sensor Alarm: Active
0x1331 | Heating Coil 1, Water | Alarm | Standard | HW1FrostAlr |  | 1x0057 | 1.01 | BI44 | 1.01 | 0 | 1 |  | Water Heating Coil 1: Frost Alarm: Active.
0x1428 | Cooling Coil | Alarm | Standard | Cool_SumAlarm |  | 1x0060 | 1.01 | BI45 | 1.01 | 0 | 1 |  | Cooling Coil: Cooling Alarm: Active.
0x1429 | Cooling Coil | Alarm | Standard | CL_Cool_DI1_Alarm |  | 1x0061 | 1.01 | BI46 | 1.01 | 0 | 1 |  | DX Cooling Coil: Alarm input 1: Active.
0x142A | Cooling Coil | Alarm | Standard | CL_Cool_DI2_Alarm |  | 1x0062 | 1.01 | BI47 | 1.01 | 0 | 1 |  | DX Cooling Coil: Alarm input 2: Active.
0x142B | Cooling Coil | Alarm | Standard | CL_Cool_DI3_Alarm |  | 1x0063 | 1.01 | BI48 | 1.01 | 0 | 1 |  | DX Cooling Coil: Alarm input 3: Active.
0x142C | Cooling Coil | Alarm | Standard | CL_Cool_DI4_Alarm |  | 1x0064 | 1.01 | BI49 | 1.01 | 0 | 1 |  | DX Cooling Coil: Alarm input 4: Active.
0x1101 | Fan, Supply | Status | Standard | SupMotorON |  | 1x0070 | 1.01 | BI50 | 1.01 | 0 | 1 |  | Supply Air Fan: ON: Active
0x1102 | Fan, Supply | Alarm | Standard | SupMotorAlarm |  | 1x0071 | 1.01 | BI51 | 1.01 | 0 | 1 |  | Supply Air Fan: Alarm: Active.
0x1A40 | Fan, Supply | Alarm | Standard | FCsupMtrAlrVlo |  | 1x0072 | 1.01 | BI52 | 1.01 | 0 | 1 |  | Supply Air Fan: Low Voltage: Alarm: Active. (only for OJ-FC)
0x1A41 | Fan, Supply | Alarm | Standard | FCsupMtrAlrVhi |  | 1x0073 | 1.01 | BI53 | 1.01 | 0 | 1 |  | Supply Air Fan: High Voltage: Alarm: Active (only for OJ-FC)
0x1A42 | Fan, Supply | Alarm | Standard | FCsupMtrAlrIhi |  | 1x0074 | 1.01 | BI54 | 1.01 | 0 | 1 |  | Supply Air Fan: High Current: Alarm: Active (only for OJ-FC, Motor Protection)
0x1A43 | Fan, Supply | Alarm | Standard | FCsupMtrAlrTmp |  | 1x0075 | 1.01 | BI55 | 1.01 | 0 | 1 |  | Supply Air Fan: High Temperature: Alarm: Active (only for OJ-FC)
0x1A44 | Fan, Supply | Alarm | Standard | FCsupMtrAlrPhs |  | 1x0076 | 1.01 | BI56 | 1.01 | 0 | 1 |  | Supply Air Fan: Phase fault: Alarm: Active (only for OJ-FC)
0x1EB8 | Fan, Extract | Alarm | Standard | Alr_EA_Controler_Ripple |  | 1x0077 | 1.01 | BI299 | 1.01 | 0 | 1 |  | Extract Air Fan: High Ripple: Alarm: Active
0x1A46 | Fan, Supply | Alarm | Standard | FCsupMtrIhiLim |  | 1x0078 | 1.01 | BI58 | 1.01 | 0 | 1 |  | Supply Air Fan: High Current Limit: Alarm: Active (Short-circuit Protection (only for OJ-FC)
0x1A45 | Fan, Supply | Alarm | Standard | Alr_SA_Controler_Ripple |  | 1x0079 | 1.01 | BI57 | 1.01 | 0 | 1 |  | Supply Air Fan: High Ripple: Alarm: Active
0x1201 | Fan, Extract | Status | Standard | ExtMotorON |  | 1x0080 | 1.01 | BI59 | 1.01 | 0 | 1 |  | Extract Fan: ON: Active
0x1A70 | Heat Exchanger | Status | Standard | EXC_ON |  | 1x0090 | 1.01 | BI68 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: Rotor Drive ON: Active. (only for OJ-DRHX)
0x1A71 | Heat Exchanger | Status | Standard | EXC_Reset |  | 1x0091 | 1.01 | BI69 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: Alarm Reset: Active. (only for OJ-DRHX)
0x1A73 | Heat Exchanger | Status | Standard | EXC_Direction |  | 1x0092 | 1.01 | BI70 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: CCW Rotation: Active. (only for OJ-DRHX)
0x1A80 | Heat Exchanger | Alarm | Standard | EXC_RotAlarm |  | 1x0093 | 1.01 | BI71 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: No Rotation: Alarm: Active (only for OJ-DRHX)
0x1A81 | Heat Exchanger | Alarm | Standard | EXC_VloAlarm |  | 1x0094 | 1.01 | BI72 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: Low Voltage: Alarm: Active (only for OJ-DRHX)
0x1A82 | Heat Exchanger | Alarm | Standard | EXC_VhiAlarm |  | 1x0095 | 1.01 | BI73 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: High Voltage: Alarm: Active (only for OJ-DRHX)
0x1A83 | Heat Exchanger | Alarm | Standard | EXC_IhiAlarm |  | 1x0096 | 1.01 | BI74 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: High Current: Alarm: Active (only for OJ-DRHX)
0x1A84 | Heat Exchanger | Alarm | Standard | EXC_TempAlarm |  | 1x0097 | 1.01 | BI75 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: High Temperature: Alarm: Active (only for OJ-DRHX)
0x1A88 | Heat Exchanger | Status | Standard | EXC_RotSignal |  | 1x0098 | 1.01 | BI76 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: Rotation signal. Active (only for OJ-DRHX)
0x1A89 | Heat Exchanger Drive | Alarm | Standard | EXC_Overload |  | 1x0099 | 1.01 | BI77 | 1.01 | 0 | 1 |  | Rotary Heat Exchanger: Torque Overload. Alarm: Active (only for OJ-DRHX)
0x1298 | Preheater Coil, Electric | Status | Standard | PH_PowReduce |  | 1x0100 | 1.01 | BI93 | 1.01 | 0 | 1 |  | Electric Pre-heating Coil: Reduced Power (insufficient flow): Active
0x1292 | Preheater Coil, Water | Status | Standard | PHFrostRegAct |  | 1x0101 | 1.01 | BI89 | 1.01 | 0 | 1 |  | Water Pre-heating Coil: Frost protection: Active
0x1294 | Preheater Coil | Status | Standard | PHHeatRelay |  | 1x0102 | 1.01 | BI91 | 1.01 | 0 | 1 |  | Pre-heating Coil: Heat Relay 1: Active
0x1295 | Preheater Coil, Water | Alarm | Standard | PH_FrzAlrCool |  | 1x0103 | 1.01 | BI301 | 1.01 | 0 | 1 |  | Water Pre-heating Coil: Frost Alarm: Active.
0x1297 | Preheater Coil, Electric | Alarm | Standard | PH_Overheat |  | 1x0104 | 1.01 | BI92 | 1.01 | 0 | 1 |  | Electric Pre-heating Coil: High temperature alarm: Active
0x129A | Preheater Coil, Water | Alarm | Standard | PH_HWBSensErr |  | 1x0105 | 1.01 | BI94 | 1.01 | 0 | 1 |  | Water Pre-heating Coil: Return Water Temperature: Sensor Alarm: Active
0x1291 | Preheater Coil, Water | Alarm | Standard | PH_FreezeAlarm |  | 1x0106 | 1.01 | BI88 | 1.01 | 0 | 1 |  | Water Pre-heating Coil: Frost Alarm: Active.
0x129C | Preheater Coil | Status | Standard | PHHeatRelay2 |  | 1x0107 | 1.01 | BI226 | 1.01 | 0 | 1 |  | Electric Pre-heater Coil: Heat Relay 2: Active
0x129D | Preheater Coil | Status | Special | PHHeatRelay3 |  | 1x0108 | 1.01 | BI176 | 1.01 | 0 | 1 |  | Electric Pre-heater Coil: Heat Relay 3: Active
0x1293 | Preheater Coil, Water | Status | Standard | PHPumpExer |  | 1x0109 | 1.01 | BI90 | 1.01 | 0 | 1 |  | Water Pre-heater Coil: Circulation Pump Exercise: Active
0x13F0 | Heat Pump | Status | Standard | HP_CoolingActv |  | 1x0110 | 1.01 | BI108 | 1.01 | 0 | 1 |  | Reversible Heat Pump: 4-way Valve in Cooling Position: Active.
0x13F2 | Heat Pump | Status | Standard | HP_De-icingAct |  | 1x0111 | 1.01 | BI109 | 1.01 | 0 | 1 |  | Reversible Heat Pump: De-icing: Active.
0x1122 | Cooling Coil | Status | Special | NO_CStopRTStat |  | 1x0112 | 1.01 | BI107 | 1.01 | 0 | 1 |  | Cooling Stopped by Room Temperature: Active
0x1123 | Heat Exchanger | Status | Standard | NO_CRecovStat |  | 1x0113 | 1.01 | BI106 | 1.01 | 0 | 1 |  | Cooling Recovery: Active.
0x1EA0 | Heat Exchanger | Alarm | Standard | AlrNoREXCali |  | 1x0114 | 1.01 | BI104 | 1.01 | 0 | 1 |  | Rotor Heat Exchanger: Ice Protection Pressure Transmitter not Calibrated: Alarm: Active
0x1EA1 | Heat Exchanger | Alarm | Standard | AlrSensREXNC |  | 1x0115 | 1.01 | BI105 | 1.01 | 0 | 1 |  | Rotor Heat Exchanger: Ice Protection Pressure Transmitter not Configured: Alarm: Active
0x1EA2 | Heat Exchanger | Alarm | Standard | AlrRexFrozen |  | 1x0116 | 1.01 | BI110 | 1.01 | 0 | 1 |  | Rotor Heat Exchanger: Blocked by Ice (High Pressure Drop Across Rotor): Alarm: Active
0x1EA3 | Heat Exchanger | Alarm | Special | AlrRexDusty |  | 1x0117 | 1.01 | BI111 | 1.01 | 0 | 1 |  | Rotor Heat Exchanger: Blocked by Dirt (High Pressure Drop Across Rotor): Alarm: Active
0x1E97 | Heat Exchanger | Alarm | Standard | AlrEXCEffToLow |  | 1x0118 | 1.01 | BI95 | 1.01 | 0 | 1 |  | Rotor Heat Exchanger: Low Recovery Efficiency: Alarm: Active
| Fan, Supply Backup | Alarm | Standard | SupBMotorAlarm |  | 1x0119 | 1.01 | BI295 | 1.01 | 0 | 1 |  | Supply Air Backup Fan: Alarm: Active
| Fan, Exhaust Backup | Alarm | Standard | ExhBMotorAlarm |  | 1x0120 | 1.01 | BI296 | 1.01 | 0 | 1 |  | Exhaust Air Backup Fan: Alarm: Active
| Heat Pump | Alarm | Standard | HP_TSExtAirErr |  | 1x0121 | 1.01 | BI311 | 1.01 | 0 | 1 |  | Reversible Heat Pump: Extract Air Temperature Downstream the Heat Pump: Sensor Alarm: Active.
| Heat Pump | Alarm | Special | Alr_HP_Deice_Incorrect |  | 1x0140 | 1.01 | BI348 | 1.01 | 0 | 1 |  | Special customer code: Reversible De-icing heat pump incorrect alarm
| Heat Pump | Alarm | Special | Alr_HP_WaterTemp |  | 1x0141 | 1.01 | BI349 | 1.01 | 0 | 1 |  | Special customer code: Reversible De-icing heat pump water temp alarm
| Damper, Fire | Alarm | Standard | Alr_FireDaNClosed |  | 1x0142 | 1.01 | BI308 | 1.01 | 0 | 1 |  | Fire Damper: Not closed: Alarm: Active.
| Damper, Fire | Alarm | Standard | Alr_FireDaNOpen |  | 1x0143 | 1.01 | BI309 | 1.01 | 0 | 1 |  | Fire Damper: Not open: Alarm: Active.
| Damper, Fire | Status | Standard | FireDmpTstActv |  | 1x0144 | 1.01 | BI310 | 1.01 | 0 | 1 |  | Fire Damper: Test sequence in Progress: Active.
0x13A0 | Heating Coil 2, Water | Alarm | Standard | HW2SensErr |  | 1x0150 | 1.01 | BI86 | 1.01 | 0 | 1 |  | Water Heating Coil 2: Return Water Temperature: Sensor Alarm: Active
0x13A1 | Heating Coil 2, Water | Alarm | Standard | HW2FrostAlr |  | 1x0151 | 1.01 | BI87 | 1.01 | 0 | 1 |  | Water Heating Coil 2: Frost Alarm: Active.
0x13A2 | Heating Coil 2, Water | Status | Standard | HW2FrostReg |  | 1x0152 | 1.01 | BI84 | 1.01 | 0 | 1 |  | Water Heating Coil 2: Frost protection: Active
0x13A3 | Heating Coil 2, Water | Status | Standard | HW2PumpExer |  | 1x0153 | 1.01 | BI85 | 1.01 | 0 | 1 |  | Water Heating Coil 2: Circulation Pump Exercise: Active
0x1401 | Heater Coil 2 | Status | Standard | Heat_RE2_DO2 |  | 1x0154 | 1.01 | BI278 | 1.01 | 0 | 1 |  | El-Heating Relay 2: Active.
0x1404 | Heating Coil 2, Electric | Status | Special | Heat_RE21_DO21 |  | 1x0155 | 1.01 | BI212 | 1.01 | 0 | 1 |  | El-Heating Relay 21: Active.
0x1405 | Heating Coil 2, Electric | Status | Special | Heat_RE22_DO22 |  | 1x0156 | 1.01 | BI213 | 1.01 | 0 | 1 |  | El-Heating Relay 22: Active.
0x1406 | Heating Coil 2, Electric | Status | Special | Heat_RE23_DO23 |  | 1x0157 | 1.01 | BI214 | 1.01 | 0 | 1 |  | El-Heating Relay 23: Active.
0x1407 | Heating Coil 2, Electric | Status | Special | Heat_RE24_DO24 |  | 1x0159 | 1.01 | BI215 | 1.01 | 0 | 1 |  | El-Heating Relay 24: Active.
0x1408 | Heating Coil 2, Electric | Status | Special | Heat_RE25_DO25 |  | 1x0160 | 1.01 | BI216 | 1.01 | 0 | 1 |  | El-Heating Relay 25: Active.
0x1110 | Temp. Sensor | Alarm | Special | AddOnTSens1Err |  | 1x0161 | 1.01 | BI79 | 1.01 | 0 | 1 |  | Temperature Sensor: Shunt Sensor 1: Alarm: Active.
0x1111 | Temp. Sensor | Alarm | Special | AddOnTSens2Err |  | 1x0162 | 1.01 | BI80 | 1.01 | 0 | 1 |  | Temperature Sensor: Shunt Sensor 2: Alarm: Active.
0x1112 | Temp. Sensor | Alarm | Special | AddOnTSens3Err |  | 1x0163 | 1.01 | BI81 | 1.01 | 0 | 1 |  | Temperature Sensor: Room Sensor 1: Alarm: Active.
0x1113 | Temp. Sensor | Alarm | Special | AddOnTSens4Err |  | 1x0164 | 1.01 | BI82 | 1.01 | 0 | 1 |  | Temperature Sensor: Room Sensor 2: Alarm: Active.
0x140B | Heating Coil 1, Water | Alarm | Standard | HW_StatLuftAlr |  | 1x0165 | 1.01 | BI302 | 1.01 | 0 | 1 |  | Frost Thermostat (digital input): Alarm: Active.
0x1E9C | Heat Exchanger | Alarm | Standard | AlrFrzBattEXC |  | 1x0166 | 1.01 | BI100 | 1.01 | 0 | 1 |  | Run Around Coil: Frost Alarm: Active.
0x1459 | Humidifier | Alarm | Standard | HumidAlrInp |  | 1x0169 | 1.01 | BI303 | 1.01 | 0 | 1 |  | Humidifier alarm status
0x13C0 | Combi Coil | Alarm | Standard | CombiTSenErr |  | 1x0170 | 1.01 | BI279 | 1.01 | 0 | 1 |  | Combi Coil: Return Water Temperature: Sensor Alarm: Active
0x13C1 | Combi Coil | Alarm | Standard | CombiFrostAlrH |  | 1x0171 | 1.01 | BI280 | 1.01 | 0 | 1 |  | Combi Coil: Frost Alarm: Active.
0x13C2 | Combi Coil | Status | Standard | CombiFrostReg |  | 1x0172 | 1.01 | BI281 | 1.01 | 0 | 1 |  | Combi Coil: Frost protection: Active
0x13C3 | Combi Coil | Status | Standard | CombiPumpExer |  | 1x0173 | 1.01 | BI282 | 1.01 | 0 | 1 |  | Combi Coil: Circulation Pump Exercise: Active
0x13C5 | Combi Coil | Status | Standard | CombiCoolRel |  | 1x0174 | 1.01 | BI283 | 1.01 | 0 | 1 |  | Combi Coil: Cooling Relay: Active.
0x13C4 | Combi Coil | Status | Standard | CombiHeatRel |  | 1x0175 | 1.01 | BI284 | 1.01 | 0 | 1 |  | Combi Coil: Heating Relay: Active.
0x1126 | Heating Coil 2 | Status | Special | Ht2DelayStatus |  | 1x0176 | 1.01 | BI113 | 1.01 | 0 | 1 |  | Special customer code: Heating Coil 2: Timer Status: Active.
0x1127 | Heating Coil 2 | Status | Special | Ht2RecBlkAct |  | 1x0177 | 1.01 | BI115 | 1.01 | 0 | 1 |  | Special customer code: Heating Coil 2: Block in Recirculation Operation: Active.
0x1128 | Heating Coil 2 | Status | Special | Ht2FlowChgAct |  | 1x0178 | 1.01 | BI112 | 1.01 | 0 | 1 |  | Special customer code: Heating Coil 2: Flow Change during Operation: Active.
0x1129 | Damper, Recirculation | Status | Special | IntRecFlowStat |  | 1x0179 | 1.01 | BI116 | 1.01 | 0 | 1 |  | Special customer code: Recirculation: Low Flow during 100% Recirculation: Active.
0x112A | Damper, Recirculation | Status | Special | RecClosDmpAct |  | 1x0180 | 1.01 | BI117 | 1.01 | 0 | 1 |  | Special customer code: Recirculation: Damper closed: Active.
0x1120 | Heating Coil 2 | Status | Special | HT2DelLimBlkNo |  | 1x0181 | 1.01 | BI114 | 1.01 | 0 | 1 |  | Special customer code: Heating Coil 2: No Limitation of Heating Power: Active.
0x1121 | AHU Controller | Status | Special | NO_CStopStat |  | 1x0182 | 1.01 | BI304 | 1.01 | 0 | 1 |  | Special customer code: Outdoor Air Cooling Stopped: Active.
0x1338 | Heating coil 1 | Status | Special | HW1RiFaActiv |  | 1x0183 | 1.01 | BI118 | 1.01 | 0 | 1 |  | Special customer code: Heating Coil 1: Max. Raise/Fall-time activated: Active.
0x1447 | Damper, Smoke evac. | Alarm | Special | Alr_FireEvaDmp |  | 1x0184 | 1.01 | BI277 | 1.01 | 0 | 1 |  | Special customer code: Smoke Evacuation Damper: Alarm: Active.
0x1990 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_LoVIn |  | 1x0185 | 1.01 | BI120 | 1.01 | 0 | 1 |  | Supply Air Fan 2: Low Voltage: Alarm: Active
0x1991 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_HiVIn |  | 1x0186 | 1.01 | BI121 | 1.01 | 0 | 1 |  | Supply Air Fan 2: High Voltage: Alarm: Active
0x1992 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Control_I_MaxAlr |  | 1x0187 | 1.01 | BI122 | 1.01 | 0 | 1 |  | Supply Air Fan 2: High Current Limit: Alarm: Active
0x1993 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_HiTemp |  | 1x0188 | 1.01 | BI123 | 1.01 | 0 | 1 |  | Supply Air Fan 2: High Temperature: Alarm: Active
0x1994 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_PhaseErr |  | 1x0189 | 1.01 | BI124 | 1.01 | 0 | 1 |  | Supply Air Fan 2: Phase Error: Alarm: Active
0x1995 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Controler_RotBlk |  | 1x0190 | 1.01 | BI126 | 1.01 | 0 | 1 |  | Supply Air Fan 2: Rotor Blocked: Alarm: Active
0x1996 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_HiIOAlr |  | 1x0191 | 1.01 | BI119 | 1.01 | 0 | 1 |  | Supply Air Fan 2: High Current: Alarm: Active
0x19B0 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_LoVIn |  | 1x0192 | 1.01 | BI128 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Low Voltage: Alarm: Active
0x19B1 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_HiVIn |  | 1x0193 | 1.01 | BI129 | 1.01 | 0 | 1 |  | Extract Air Fan 2: High Voltage: Alarm: Active
0x19B2 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Control_I_MaxAlr |  | 1x0194 | 1.01 | BI130 | 1.01 | 0 | 1 |  | Extract Air Fan 2: High Current Limit: Alarm: Active
0x19B3 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_HiTemp |  | 1x0195 | 1.01 | BI131 | 1.01 | 0 | 1 |  | Extract Air Fan 2: High Temperature: Alarm: Active
0x19B4 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_PhaseErr |  | 1x0196 | 1.01 | BI132 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Phase Error: Alarm: Active
0x19B5 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Controler_RotBlk |  | 1x0197 | 1.01 | BI134 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Rotor Blocked: Alarm: Active
0x19B6 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_HiIOAlr |  | 1x0198 | 1.01 | BI127 | 1.01 | 0 | 1 |  | Extract Air Fan 2: High Current: Alarm: Active
0x1EA6 | Temp. sensor | Alarm | Standard | AlrTTH6202Com |  | 1x0199 | 1.01 | BI155 | 1.01 | 0 | 1 |  | Temperature Sensor: TTH-6202: Communication Error: Alarm: Active.
0x1950 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_LoVIn |  | 1x0200 | 1.01 | BI138 | 1.01 | 0 | 1 |  | Supply Air Fan: Low Voltage: Alarm: Active
0x1951 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_HiVIn |  | 1x0201 | 1.01 | BI139 | 1.01 | 0 | 1 |  | Supply Air Fan: High Voltage: Alarm: Active
0x1952 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_HiIOAlr |  | 1x0202 | 1.01 | BI140 | 1.01 | 0 | 1 |  | Supply Air Fan: High Current: Alarm: Active
0x1953 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_HiTemp |  | 1x0203 | 1.01 | BI141 | 1.01 | 0 | 1 |  | Supply Air Fan: High Temperature: Alarm: Active
0x1954 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_PhaseErr |  | 1x0204 | 1.01 | BI142 | 1.01 | 0 | 1 |  | Supply Air Fan: Phase Error: Alarm: Active
0x1955 | Fan, Supply | Alarm | Standard | Alr_SA_Controler_RotBlk |  | 1x0205 | 1.01 | BI144 | 1.01 | 0 | 1 |  | Supply Air Fan: Rotor Blocked: Alarm: Active
0x1956 | Fan, Supply | Alarm | Standard | Alr_SA_ControlerI_MaxAlr |  | 1x0206 | 1.01 | BI137 | 1.01 | 0 | 1 |  | Supply Air Fan: High Current Limit: Alarm: Active
0x1970 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_LoVIn |  | 1x0207 | 1.01 | BI146 | 1.01 | 0 | 1 |  | Extract Air Fan: Low Voltage: Alarm: Active
0x1971 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_HiVIn |  | 1x0208 | 1.01 | BI147 | 1.01 | 0 | 1 |  | Extract Air Fan: High Voltage: Alarm: Active
0x1972 | Fan, Extract | Alarm | Standard | Alr_EA_ControlerI_MaxAlr |  | 1x0209 | 1.01 | BI148 | 1.01 | 0 | 1 |  | Extract Air Fan: High Current: Alarm: Active
0x1973 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_HiTemp |  | 1x0210 | 1.01 | BI149 | 1.01 | 0 | 1 |  | Extract Air Fan: High Temperature: Alarm: Active
0x1974 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_PhaseErr |  | 1x0211 | 1.01 | BI150 | 1.01 | 0 | 1 |  | Extract Air Fan: Phase Error: Alarm: Active
0x1975 | Fan, Extract | Alarm | Standard | Alr_EA_Controler_RotBlk |  | 1x0212 | 1.01 | BI152 | 1.01 | 0 | 1 |  | Extract Air Fan: Rotor Blocked: Alarm: Active
0x1976 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_HiIOAlr |  | 1x0213 | 1.01 | BI145 | 1.01 | 0 | 1 |  | Extract Air Fan: High Current Limit: Alarm: Active
0x1E35 | IO Extension Module | Alarm | Standard | AlrExtIO1_Comm |  | 1x0214 | 1.01 | BI158 | 1.01 | 0 | 1 |  | Extention IO-Module no. 1: Communication Error: Alarm: Active.
0x1E36 | IO Extension Module | Alarm | Standard | AlrExtIO2_Comm |  | 1x0215 | 1.01 | BI159 | 1.01 | 0 | 1 |  | Extention IO-Module no. 2: Communication Error: Alarm: Active.
0x1E84 | IO Extension Module | Alarm | Standard | AlrExtIO3_Comm |  | 1x0216 | 1.01 | BI160 | 1.01 | 0 | 1 |  | Extention IO-Module no. 3: Communication Error: Alarm: Active.
0x1E85 | IO Extension Module | Alarm | Standard | AlrExtIO4_Comm |  | 1x0217 | 1.01 | BI161 | 1.01 | 0 | 1 |  | Extention IO-Module no. 4: Communication Error: Alarm: Active.
0x1E86 | IO Extension Module | Alarm | Standard | AlrExtIO5_Comm |  | 1x0218 | 1.01 | BI162 | 1.01 | 0 | 1 |  | Extention IO-Module no. 5: Communication Error: Alarm: Active.
0x1E87 | IO Extension Module | Alarm | Standard | AlrExtIO6_Comm |  | 1x0219 | 1.01 | BI163 | 1.01 | 0 | 1 |  | Extention IO-Module no. 6: Communication Error: Alarm: Active.
0x1E88 | IO Extension Module | Alarm | Standard | AlrExtIO7_Comm |  | 1x0220 | 1.01 | BI164 | 1.01 | 0 | 1 |  | Extention IO-Module no. 7: Communication Error: Alarm: Active.
0x1E8F | IO Extension Module | Alarm | Standard | AlrExtIO8_Comm |  | 1x0221 | 1.01 | BI165 | 1.01 | 0 | 1 |  | Extention IO-Module no. 8: Communication Error: Alarm: Active.
0x1EA9 | Temp. Sensor | Alarm | Standard | Alr_AddOnSens1 |  | 1x0222 | 1.01 | BI167 | 1.01 | 0 | 1 |  | Temperature Sensor: Add on Sensor 1: Alarm: Active.
0x1EAA | Temp. Sensor | Alarm | Standard | Alr_AddOnSens2 |  | 1x0223 | 1.01 | BI168 | 1.01 | 0 | 1 |  | Temperature Sensor: Add on Sensor 2: Alarm: Active.
0x1EAB | Temp. Sensor | Alarm | Standard | Alr_AddOnSens3 |  | 1x0224 | 1.01 | BI169 | 1.01 | 0 | 1 |  | Temperature Sensor: Add on Sensor 3: Alarm: Active.
0x1EAC | Temp. Sensor | Alarm | Standard | Alr_AddOnSens4 |  | 1x0225 | 1.01 | BI170 | 1.01 | 0 | 1 |  | Temperature Sensor: Add on Sensor 4: Alarm: Active.
0x03BA | Cooling, DX | Status | Special | ROHRiFaActiv |  | 1x0226 | 1.01 | BI174 | 1.01 | 0 | 1 |  | Special customer code: DX Cooling: Rise-Falltime DX-CO2-Cooling: Active.
0x13C9 | Combi Coil | Status | Standard | Cmb2CoolRel |  | 1x0227 | 1.01 | BI173 | 1.01 | 0 | 1 |  | Combi Coil: Cooling Relay no. 2: Active.
0x1959 | Fan, Supply | Alarm | Standard | ECsupEEP_Err |  | 1x0228 | 1.01 | BI178 | 1.01 | 0 | 1 |  | Supply Air Fan: EEprom Error: Alarm: Active.
0x1999 | Fan 2, Supply | Alarm | Standard | EC2supEEP_Err |  | 1x0229 | 1.01 | BI179 | 1.01 | 0 | 1 |  | Supply Air Fan 2: EEprom Error: Alarm: Active.
0x1979 | Fan, Extract | Alarm | Standard | ECextEEP_Err |  | 1x0230 | 1.01 | BI180 | 1.01 | 0 | 1 |  | Extract Air Fan: EEprom Error: Alarm: Active.
0x19B9 | Fan 2, Extract | Alarm | Standard | EC2extEEP_Err |  | 1x0231 | 1.01 | BI181 | 1.01 | 0 | 1 |  | Extract Air Fan 2: EEprom Error: Alarm: Active.
0x1EAD | Temp. Sensor | Alarm | Standard | TTH6040ComAlr |  | 1x0232 | 1.01 | BI182 | 1.01 | 0 | 1 |  | Temperature Sensor: TTH-6040-W Room: Communication Error: Alarm: Active.
0x1EAE | Cooling, DX | Alarm | Special | LowOilDXHPAlr |  | 1x0233 | 1.01 | BI183 | 1.01 | 0 | 1 |  | Special customer code: Cooling Compressor: Low Oil Level: Alarm: Active.
0x1EAF | AHU Controller | Fire | Special | Alr_FireManStop |  | 1x0234 | 1.01 | BI203 | 1.01 | 0 | 1 |  | Special customer code: Fire Stop: Active.
0x1EB0 | Damper, Smoke evac. | Smoke | Special | Alr_SmokEvacAct |  | 1x0235 | 1.01 | BI204 | 1.01 | 0 | 1 |  | Special customer code: Smoke Evacuation: Active.
0x1EB1 | Temp. Room | Alarm | Standard | Alr_BMS_Room_TS_OOR |  | 1x0236 | 1.01 | BI201 | 1.01 | 0 | 1 |  | BMS Room Temperature: Value Out of Range: Alarm: Active.
0x1EB2 | Temp. Out door | Alarm | Standard | Alr_BMS_OA_TS_OOR |  | 1x0237 | 1.01 | BI202 | 1.01 | 0 | 1 |  | BMS Outdoor Temperature: Value Out of Range: Alarm: Active.
0x1EB3 | Fan, Smoke evac. | Alarm | Special | AlrSmokEvaFan |  | 1x0238 | 1.01 | BI205 | 1.01 | 0 | 1 |  | Special customer code: Smoke Evacuation Fan: Alarm: Active.
0x1F2D | Temp. Sensor | Alarm | Standard | TTH_6040OA_PortA_Com |  | 1x0239 | 1.01 | BI294 | 1.01 | 0 | 1 |  | Temperature Sensor: TTH-6040-O Outdoor: Communication Error (Port A): Alarm: Active
0x1015 | Damper, Fresh air | Status | Standard | DO_OA_BigDamp_Relay |  | 1x0240 | 1.01 | BI206 | 1.01 | 0 | 1 |  | Outdoor Air / Exhaust Air Damper: Open: Active.
0x1016 | Damper, Supply air | Status | Standard | DO_SA_BigDamp_Relay |  | 1x0241 | 1.01 | BI207 | 1.01 | 0 | 1 |  | Supply Air Damper: Open: Active.
0x1017 | Damper, Recirculation | Status | Standard | DO_REC_BigDamp_Relay |  | 1x0242 | 1.01 | BI208 | 1.01 | 0 | 1 |  | Recirculation Air Damper: Open: Active.
0x1301 | Temp. Out door | Alarm | Standard | ExOutDSensErr |  | 1x0243 | 1.01 | BI209 | 1.01 | 0 | 1 |  | External Outdoor Temperature: Sensor Alarm: Active.
0x1290 | Preheater Coil, Water | Alarm | Standard | Alr_PreheatAirSens |  | 1x0244 | 1.01 | BI210 | 1.01 | 0 | 1 |  | Pre-heater Temperature: Sensor Alarm: Active.
0x1351 | Cooling Coil | Alarm | Standard | CL_CW_TSensErr |  | 1x0245 | 1.01 | BI211 | 1.01 | 0 | 1 |  | Water Cooling Coil: Inlet Water Temperature: Sensor Alarm: Active.
0x1409 | Heating Coil 1, Electric | Status | Standard | Heat_RE26 |  | 1x0246 | 1.01 | BI217 | 1.01 | 0 | 1 |  | El-Heating Relay 26: Active.
0x140A | Combi Coil | Status | Standard | Combi_PumpRE |  | 1x0247 | 1.01 | BI218 | 1.01 | 0 | 1 |  | Combi Coil: Circulation Pump On: Active
0x1486 | Heating Coil 2, Electric | Alarm | Standard | EL2_OverHtBac |  | 1x0248 | 1.01 | BI221 | 1.01 | 0 | 1 |  | Electric Heating Coil 2: High Temperature Alarm: Active
0x1EC4 | Heating Coil 2, Electric | Alarm | Standard | AlrBat2Contact |  | 1x0249 | 1.01 | BI222 | 1.01 | 0 | 1 |  | Electric Heating Coil 2: Relay Stuck: Active
0x1EB4 | Filter | Alarm | Standard | OutFiltAlrOn |  | 1x0250 | 1.01 | BI223 | 1.01 | 0 | 1 |  | Supply Air Filter: Timer Expired: Alarm: Active.
0x1EB5 | Filter | Alarm | Standard | ExtFiltAlrOn |  | 1x0251 | 1.01 | BI224 | 1.01 | 0 | 1 |  | Exhaust Air filter: Timer Expired: Alarm: Active.
0x1EB6 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_PowLim |  | 1x0252 | 1.01 | BI229 | 1.01 | 0 | 1 |  | Supply Air Fan: Power Limit Alarm: Active
0x1EB7 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_PowLim |  | 1x0253 | 1.01 | BI230 | 1.01 | 0 | 1 |  | Extract Air Fan: Power Limit Alarm: Active
0x1EBE | Fan, Supply | Alarm | Standard | Alr_SA_Controler_RotBlk |  | 1x0254 | 1.01 | BI231 | 1.01 | 0 | 1 |  | Supply Air Fan: Rotor Blocked Alarm: Active.
0x1EBF | Fan, Extract | Alarm | Standard | Alr_EA_Controler_RotBlk |  | 1x0255 | 1.01 | BI232 | 1.01 | 0 | 1 |  | Extract Air Fan: Rotor Blocked Alarm: Active.
0x1F00 | Fan, Supply | Alarm | Standard | Alr_SA_Controler_IStop |  | 1x0256 | 1.01 | BI233 | 1.01 | 0 | 1 |  | Supply Air Fan: Intern Stop Alarm: Active.
0x1F02 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Controler_IStop |  | 1x0257 | 1.01 | BI235 | 1.01 | 0 | 1 |  | Supply Air Fan 2: Intern Stop Alarm: Active.
0x1F01 | Fan, Extract | Alarm | Standard | Alr_EA_Controler_IStop |  | 1x0258 | 1.01 | BI234 | 1.01 | 0 | 1 |  | Extract Air Fan: Intern Stop Alarm: Active.
0x1F03 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Controler_IStop |  | 1x0259 | 1.01 | BI236 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Intern Stop Alarm: Active
0x13CE | Combi Coil | Status | Standard | CmbHeatState |  | 1x0260 | 1.01 | BI237 | 1.01 | 0 | 1 |  | Combi Coil: Heating: Active.
0x13CF | Combi Coil | Status | Standard | CmbCoolState |  | 1x0261 | 1.01 | BI238 | 1.01 | 0 | 1 |  | Combi Coil: Cooling: Active.
0x1487 | Preheater coil, electric | Alarm | Standard | Pre_OverHtBac |  | 1x0262 | 1.01 | BI239 | 1.01 | 0 | 1 |  | Electric Pre-heating Coil: High Temperature Alarm: Active
0x1E90 | Preheater coil, electric | Alarm | Standard | AlrPrhContact |  | 1x0263 | 1.01 | BI240 | 1.01 | 0 | 1 |  | Electric Pre-heating Coil: Relay stuck: Active
0x19CC | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_HiIOAlr |  | 1x0266 | 1.01 | BI243 | 1.01 | 0 | 1 |  | Supply Air Fan 2: High Current: Alarm: Active
0x19CD | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_HiIOAlr |  | 1x0267 | 1.01 | BI244 | 1.01 | 0 | 1 |  | Extract Air Fan 2: High Current: Alarm: Active
0x1F2A | Energy Meeter | Alarm | Standard | Alr_CommCVMMini |  | 1x0268 | 1.01 | BI305 | 1.01 | 0 | 1 |  | CVM Energy Meter: Communication Error: Alarm: Active.
0x1F2B | Energy Meter | Alarm | Standard | Alr_CommCVMCool |  | 1x0269 | 1.01 | BI306 | 1.01 | 0 | 1 |  | CVM Cooling Energy Meter: Communication Error: Alarm: Active.
0x19CE | Fan, Supply | Alarm | Standard | AlrSupFanStop |  | 1x0270 | 1.01 | BI245 | 1.01 | 0 | 1 |  | Supply Fan: Stopped: Alarm: Active.
0x19CF | HMI display | Alarm | Standard | AlrComHMI20 |  | 1x0271 | 1.01 | BI307 | 1.01 | 0 | 1 |  | HMI-20T Touchpanel: Communication Error: Alarm: Active.
0x19D6 | Damper, Smoke evac. | Alarm | Special | AlrSMEvacDmp |  | 1x0272 | 1.01 | BI246 | 1.01 | 0 | 1 |  | Special customer code: Smoke Evacuation Damper: Position not reached: Alarm: Active.
0x19D7 | Damper, Smoke evac. | Alarm | Special | AlrSMBPassDmp |  | 1x0273 | 1.01 | BI247 | 1.01 | 0 | 1 |  | Special customer code: Smoke Bypass Damper: Position not reached: Alarm: Active.
0x1F20 | Pressure | Alarm | Standard | Alr_DPTH_1Com |  | 1x0274 | 1.01 | BI248 | 1.01 | 0 | 1 |  | Pressure transmitter PTH-6202-2 No. 1: Communication Error: Alarm: Active.
0x1F21 | Pressure | Alarm | Standard | Alr_DPTH_2Com |  | 1x0275 | 1.01 | BI249 | 1.01 | 0 | 1 |  | Pressure transmitter PTH-6202-2 No. 2: Communication Error: Alarm: Active.
0x1F22 | Pressure | Alarm | Standard | Alr_DPTH_3Com |  | 1x0276 | 1.01 | BI250 | 1.01 | 0 | 1 |  | Pressure transmitter PTH-6202-2 No. 3: Communication Error: Alarm: Active.
0x1F23 | Pressure | Alarm | Standard | Alr_DPTH_4Com |  | 1x0277 | 1.01 | BI251 | 1.01 | 0 | 1 |  | Pressure transmitter PTH-6202-2 No. 4: Communication Error: Alarm: Active.
0x1F24 | Pressure | Alarm | Standard | Alr_DPTH_5Com |  | 1x0278 | 1.01 | BI252 | 1.01 | 0 | 1 |  | Pressure transmitter PTH-6202-2 No. 5: Communication Error: Alarm: Active.
0x1F27 | Filter | Alarm | Standard | Alr_SAFilt2TimerAlrOn |  | 1x0279 | 1.01 | BI255 | 1.01 | 0 | 1 |  | Supply Air Filter 2: Timer Expired: Alarm: Active.
0x1F28 | Filter | Alarm | Standard | Alr_EAFilt2TimerAlrOn |  | 1x0280 | 1.01 | BI256 | 1.01 | 0 | 1 |  | Extract Air Filter 2: Timer Expired: Alarm: Active.
0x1ECE | Heating | Alarm | Standard | Alr_Frost_OA_Luftsensor |  | 1x0281 | 1.01 | BI83 | 1.01 | 0 | 1 |  | Frost Thermostat: Outdoor Air (digital input): Alarm: Active.
0x1998 | Fan 2, Supply | Alarm | Standard | Alr_SA2_Contr_Rot_DirErr |  | 1x0282 | 1.01 | BI125 | 1.01 |  |  |  | Supply Air Fan 2: Rotation Direction Alarm: Active.
0x19B8 | Fan 2, Extract | Alarm | Standard | Alr_EA2_Contr_Rot_DirErr |  | 1x0283 | 1.01 | BI133 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Rotation Direction Alarm: Active.
0x1EA4 | Fan 2, Supply | Alarm | Standard | Alr_SA2Controler_Com |  | 1x0284 | 1.01 | BI135 | 1.01 | 0 | 1 |  | Supply Air Fan 2: Communication Error: Alarm: Active.
0x1EA5 | Fan 2, Extract | Alarm | Standard | Alr_EA2Controler_Com |  | 1x0285 | 1.01 | BI136 | 1.01 | 0 | 1 |  | Extract Air Fan 2: Communication Error: Alarm: Active.
0x1958 | Fan, Supply | Alarm | Standard | Alr_SA_Contr_Rot_DirErr |  | 1x0286 | 1.01 | BI143 | 1.01 | 0 | 1 |  | Supply Air Fan: Rotation Direction Alarm: Active.
0x1978 | Fan, Extract | Alarm | Standard | Alr_EA_Contr_Rot_DirErr |  | 1x0287 | 1.01 | BI151 | 1.01 | 0 | 1 |  | Extract Air Fan: Rotation Direction Alarm: Active.
0x1E6C | Fan, Supply | Alarm | Standard | Alr_SA_Controler_Comm |  | 1x0288 | 1.01 | BI153 | 1.01 | 0 | 1 |  | Supply Air Fan: Communication Error: Alarm: Active.
0x1E6D | Fan, Extract | Alarm | Standard | Alr_EA_Controler_Comm |  | 1x0289 | 1.01 | BI154 | 1.01 | 0 | 1 |  | Extract Air Fan: Communication Error: Alarm: Active.
0x1EF6 | Damper, Smoke evac. | Alarm | Special | Alr_BDSmokeCom_Error |  | 1x0290 | 1.01 | BI156 | 1.01 | 0 | 1 |  | Special customer code: Belimo Smoke Evacuation Damper: Communication Error: Alarm: Active.
0x1E76 | Damper, Smoke evac. | Alarm | Special | Alr_BDSmokePos_Error |  | 1x0291 | 1.01 | BI157 | 1.01 | 0 | 1 |  | Special customer code: Belimo Smoke Evacuation Damper: Position not reached: Alarm: Active.
0x1EA8 | Temp. Supply | Alarm | Special | AlrSupTemp2 |  | 1x0292 | 1.01 | BI166 | 1.01 | 0 | 1 |  | Special customer code: Supply Air Temperature 2: Sensor Alarm: Active
0x1E56 | Fan, Supply | Alarm | Standard | Alr_SA_Controler |  | 1x0293 | 1.01 | BI171 | 1.01 | 0 | 1 |  | Supply Fan: Alarm: Active.
0x1E57 | Fan, Extract | Alarm | Standard | Alr_EA_Controler |  | 1x0294 | 1.01 | BI172 | 1.01 | 0 | 1 |  | Extract Fan: Alarm: Active.
0x1E98 | Fan, ATV drive | Alarm | Special | AlrAtvSupComm |  | 1x0295 | 1.01 | BI96 | 1.01 | 0 | 1 |  | Special customer code: Supply Fan ATV Drive: Communication Error: Alarm: Active.
0x1E99 | Fan, ATV drive | Alarm | Special | AlrAtvExtComm |  | 1x0296 | 1.01 | BI97 | 1.01 | 0 | 1 |  | Special customer code: Extract Fan ATV Drive: Communication Error: Alarm: Active.
0x1E9A | Fan, ATV drive | Alarm | Special | AlrAtvSupFC |  | 1x0297 | 1.01 | BI98 | 1.01 | 0 | 1 |  | Special customer code: Supply Fan ATV Drive: Alarm: Active.
0x1E9B | Fan, ATV drive | Alarm | Special | AlrAtvExtFC |  | 1x0298 | 1.01 | BI99 | 1.01 | 0 | 1 |  | Special customer code: Extract Fan ATV Drive: Alarm: Active.
0x1E9D | Preheater Coil, Electric | Alarm | Special | AlrDeIceCont |  | 1x0299 | 1.01 | BI101 | 1.01 | 0 | 1 |  | Special customer code: Electric De-icing Coil: Relay stuck: Active
0x1E9E | Preheater Coil, Electric | Alarm | Special | AlrDeIceOverh |  | 1x0300 | 1.01 | BI102 | 1.01 | 0 | 1 |  | Special customer code: Electric De-icing Coil: High Temperature Alarm: Active
0x1E9F | Preheater Coil, Electric | Alarm | Special | AlrDeIceReduc |  | 1x0301 | 1.01 | BI103 | 1.01 | 0 | 1 |  | Special customer code: Electric De-icing Coil: Reduced Power (insufficient flow): Active
0x1600 | Zone, PIR | Status | Standard | ZM_PIR |  | 1x0303 | 1.01 | BI257 | 1.01 | 0 | 1 |  | Zone Control: PIR Active in one or more Zones.
0x1610 | Zone 1 | Status | Standard | ZM1_WinFrost |  | 1x0304 | 1.01 | BI258 | 1.01 | 0 | 1 |  | Zone Module 1: Window Contact or Frost Protection: Active.
0x1611 | Zone 1 | Status | Standard | ZM1_PIR |  | 1x0305 | 1.01 | BI259 | 1.01 | 0 | 1 |  | Zone Module 1: PIR Active.
0x1612 | Zone 1 | Alarm | Standard | ZM1_RoomTmpErr |  | 1x0306 | 1.01 | BI260 | 1.01 | 0 | 1 |  | Zone Module 1: Room Temperature Sensor Error: Alarm: Active.
0x1613 | Zone 1 | Alarm | Standard | ZM1_SupTempErr |  | 1x0307 | 1.01 | BI261 | 1.01 | 0 | 1 |  | Zone Module 1: Supply Air Temperature Sensor Error: Alarm: Active.
0x1620 | Zone 2 | Status | Standard | ZM2_WinFrost |  | 1x0308 | 1.01 | BI262 | 1.01 | 0 | 1 |  | Zone Module 2: Window Contact or Frost Protection: Active.
0x1621 | Zone 2 | Status | Standard | ZM2_PIR |  | 1x0309 | 1.01 | BI263 | 1.01 | 0 | 1 |  | Zone Module 2: PIR Active.
0x1622 | Zone 2 | Alarm | Standard | ZM2_RoomTmpErr |  | 1x0310 | 1.01 | BI264 | 1.01 | 0 | 1 |  | Zone Module 2: Room Temperature Sensor Error: Alarm: Active.
0x1623 | Zone 2 | Alarm | Standard | ZM2_SupTempErr |  | 1x0311 | 1.01 | BI265 | 1.01 | 0 | 1 |  | Zone Module 2: Supply Air Temperature Sensor Error: Alarm: Active.
0x1630 | Zone 3 | Status | Standard | ZM3_WinFrost |  | 1x0312 | 1.01 | BI266 | 1.01 | 0 | 1 |  | Zone Module 3: Window Contact or Frost Protection: Active.
0x1631 | Zone 3 | Status | Standard | ZM3_PIR |  | 1x0313 | 1.01 | BI267 | 1.01 | 0 | 1 |  | Zone Module 3: PIR Active.
0x1632 | Zone 3 | Alarm | Standard | ZM3_RoomTmpErr |  | 1x0314 | 1.01 | BI268 | 1.01 | 0 | 1 |  | Zone Module 3: Room Temperature Sensor Error: Alarm: Active.
0x1633 | Zone 3 | Alarm | Standard | ZM3_SupTempErr |  | 1x0315 | 1.01 | BI269 | 1.01 | 0 | 1 |  | Zone Module 3: Supply Air Temperature Sensor Error: Alarm: Active.
0x1640 | Zone 4 | Status | Standard | ZM4_WinFrost |  | 1x0316 | 1.01 | BI270 | 1.01 | 0 | 1 |  | Zone Module 4: Window Contact or Frost Protection: Active.
0x1641 | Zone 4 | Status | Standard | ZM4_PIR |  | 1x0317 | 1.01 | BI271 | 1.01 | 0 | 1 |  | Zone Module 4: PIR Active.
0x1642 | Zone 4 | Alarm | Standard | ZM4_RoomTmpErr |  | 1x0318 | 1.01 | BI272 | 1.01 | 0 | 1 |  | Zone Module 4: Room Temperature Sensor Error: Alarm: Active.
0x1643 | Zone 4 | Alarm | Standard | ZM4_SupTempErr |  | 1x0319 | 1.01 | BI273 | 1.01 | 0 | 1 |  | Zone Module 4: Supply Air Temperature Sensor Error: Alarm: Active.
0x1421 | Cooling, DX | Status | Standard | Cool_RE2 |  | 1x0320 | 1.01 | BI274 | 1.01 | 0 | 1 |  | Cooling Relay 2: Active
0x1422 | Cooling, DX | Status | Standard | Cool_RE3 |  | 1x0321 | 1.01 | BI275 | 1.01 | 0 | 1 |  | Cooling Relay 3: Active
0x1423 | Cooling, DX | Status | Standard | Cool_RE4 |  | 1x0322 | 1.01 | BI276 | 1.01 | 0 | 1 |  | Cooling Relay 4: Active
0x1F3C | Fan Wall, Supply | Alarm | Standard | SupFanWallAlr |  | 1x0323 | 1.01 | BI286 | 1.01 | 0 | 1 |  | Supply Fan Wall: Alarm: Active.
0x1F3D | Fan Wall, Extract | Alarm | Standard | ExtFanWallAlr |  | 1x0324 | 1.01 | BI287 | 1.01 | 0 | 1 |  | Extract Fan Wall: Alarm: Active.
0x10D0 | Damper, Extract | Status | Standard | ExtDamperSig |  | 1x0325 | 1.01 | BI288 | 1.01 | 0 | 1 |  | Extract Air Damper: Open: Active.
0x10D1 | Damper, Exhaust | Status | Standard | ExhDamperSig |  | 1x0326 | 1.01 | BI289 | 1.01 | 0 | 1 |  | Exhaust Air Damper: Open: Active.
0x10D2 | Damper, Backup Exhaust | Status | Standard | ExhBDamperSig |  | 1x0327 | 1.01 | BI290 | 1.01 | 0 | 1 |  | Exhaust Air Backup Damper: Open: Active.
0x10D3 | Damper, Backup Supply | Status | Standard | SupBDamperSig |  | 1x0328 | 1.01 | BI291 | 1.01 | 0 | 1 |  | Supply Air Backup Damper: Open: Active.
0x19DB | Fan, Supply Backup | Alarm | Standard | AlrSupBMtr |  | 1x0329 | 1.01 | BI292 | 1.01 | 0 | 1 |  | Supply Air Backup Fan: Alarm: Active
0x19DC | Fan, Exhaust Backup | Alarm | Standard | AlrExhBMtr |  | 1x0330 | 1.01 | BI293 | 1.01 | 0 | 1 |  | Exhaust Air Backup Fan: Alarm: Active
0x1F3E | AHU Controller | Alarm | Special | AggBlKAlr |  | 1x0331 | 1.01 | BI312 | 1.01 | 0 | 1 |  | Special customer code: AHU start blocked. Alarm: Active.
0x148B | Heating Coil, Electric | Alarm | Special | FireEHtCoilAlr |  | 1x0332 | 1.01 | BI313 | 1.01 | 0 | 1 |  | Special customer code: El-Heater Firethermostat: Alarm: Active
0x148C | Preheater Coil, Electric | Alarm | Special | FireEPrHeatAlr |  | 1x0333 | 1.01 | BI314 | 1.01 | 0 | 1 |  | Special customer code: El-Pre-Heater Firethermostat: Alarm: Active
0x1F2F | Heat Pump | Alarm | Special | AlrCommDaikin |  | 1x0334 | 1.01 | BI315 | 1.01 | 0 | 1 |  | Special customer code: Daikin EVKit: Communication Error: Alarm: Active.
0x19DD | Heat Pump | Alarm | Special | AlrDaikinWrn |  | 1x0335 | 1.01 | BI316 | 1.01 | 0 | 1 |  | Special customer code: Daikin EVKit: Warning: Active
0x19DE | Heat Pump | Alarm | Special | AlrDaikinAlr |  | 1x0336 | 1.01 | BI317 | 1.01 | 0 | 1 |  | Special customer code: Daikin EVKit: Alarm: Active.
0x19DF | Heat Pump | Alarm | Special | AlrDaikinErr |  | 1x0337 | 1.01 | BI318 | 1.01 | 0 | 1 |  | Special customer code: Daikin EVKit: Error: Active.
0x1550 | Compressor | Alarm | Standard | DriveCmpCmAlr |  | 1x0340 | 1.01 | BI320 | 1.01 | 0 | 1 |  | Drives Compressor: Communication Error: Alarm: Active.
0x1551 | Compressor | Alarm | Standard | DrCmp_IHghAlr |  | 1x0341 | 1.01 | BI321 | 1.01 | 0 | 1 |  | Drives Compressor: High Current: Alarm: Active.
0x1552 | Compressor | Alarm | Standard | DrCmpLwVltAlr |  | 1x0342 | 1.01 | BI322 | 1.01 | 0 | 1 |  | Drives Compressor: Low Voltage: Alarm: Active.
0x1553 | Compressor | Alarm | Standard | DrCmpHghVltAlr |  | 1x0343 | 1.01 | BI323 | 1.01 | 0 | 1 |  | Drives Compressor: High Voltage: Alarm: Active.
0x1554 | Compressor | Alarm | Standard | DrCmpHiTmpAlr |  | 1x0344 | 1.01 | BI324 | 1.01 | 0 | 1 |  | Drives Compressor: High Temperature: Alarm: Active.
0x1555 | Compressor | Alarm | Standard | DrCmpInpPhAlr |  | 1x0345 | 1.01 | BI325 | 1.01 | 0 | 1 |  | Drives Compressor: Input Phase Error: Alarm: Active.
0x1556 | Compressor | Alarm | Standard | DrCmpRtrBlkAlr |  | 1x0346 | 1.01 | BI326 | 1.01 | 0 | 1 |  | Drives Compressor: Rotor Blocked: Alarm: Active.
0x1557 | Compressor | Alarm | Standard | DrCmpILimitAlr |  | 1x0347 | 1.01 | BI327 | 1.01 | 0 | 1 |  | Drives Compressor: Current Limit: Alarm: Active.
0x1558 | Compressor | Alarm | Standard | DrCmpVLimitAlr |  | 1x0348 | 1.01 | BI328 | 1.01 | 0 | 1 |  | Drives Compressor: Voltage Limit: Alarm: Active.
0x1559 | Compressor | Alarm | Standard | DrCmpRtrDirAlr |  | 1x0349 | 1.01 | BI329 | 1.01 | 0 | 1 |  | Drives Compressor: Rotor Rotation Error: Alarm: Active.
0x155A | Compressor | Alarm | Standard | DrCmpEEPROM |  | 1x0350 | 1.01 | BI330 | 1.01 | 0 | 1 |  | Drives Compressor: Internal Error: Alarm: Active.
0x155B | Compressor | Alarm | Standard | DrCmpIntrnStp |  | 1x0351 | 1.01 | BI331 | 1.01 | 0 | 1 |  | Drives Compressor: Internal Stop: Alarm: Active.
0x155C | Compressor | Alarm | Standard | DrCmpEarthFlt |  | 1x0352 | 1.01 | BI332 | 1.01 | 0 | 1 |  | Drives Compressor: Earth Error: Alarm: Active.
0x155D | Compressor | Alarm | Standard | DrCmpPhaseErr |  | 1x0353 | 1.01 | BI333 | 1.01 | 0 | 1 |  | Drives Compressor: Motor Phase Error: Alarm: Active.
0x155E | Compressor | Alarm | Standard | DrCmpComErrMOC |  | 1x0354 | 1.01 | BI334 | 1.01 | 0 | 1 |  | Drives Compressor: Internal MOC Communication Error: Alarm: Active.
0x155F | Compressor | Alarm | Standard | DrCmp24VOvrlad |  | 1x0355 | 1.01 | BI335 | 1.01 | 0 | 1 |  | Drives Compressor: +24V DC Output Overload: Alarm: Active.
0x1560 | Compressor | Alarm | Standard | DrCmpMOCinBoot |  | 1x0356 | 1.01 | BI336 | 1.01 | 0 | 1 |  | Drives Compressor: Internal Bootloader Error: Alarm: Active.
0x1561 | Compressor | Alarm | Standard | DrCmpComErrIOM |  | 1x0357 | 1.01 | BI337 | 1.01 | 0 | 1 |  | Drives Compressor: Internal Communication Error to IO module: Alarm: Active.
0x1562 | Compressor | Alarm | Standard | DrCmpOverheat |  | 1x0358 | 1.01 | BI338 | 1.01 | 0 | 1 |  | Drives Compressor: Motor Overheated: Alarm: Active.
0x1563 | Compressor | Alarm | Standard | DrCmpErStrtup |  | 1x0359 | 1.01 | BI339 | 1.01 | 0 | 1 |  | Drives Compressor: Start Up Error: Alarm: Active.
0x1564 | Compressor | Alarm | Standard | DrCmpPrssRlx |  | 1x0360 | 1.01 | BI340 | 1.01 | 0 | 1 |  | Drives Compressor: Pressure Relax Error: Alarm: Active.
0x1565 | Compressor | Alarm | Standard | DrCmpMaxStarts |  | 1x0361 | 1.01 | BI341 | 1.01 | 0 | 1 | 1 | Drives Compressor: Max Start No. Limit Reached: Alarm: Active.
0x1566 | Compressor | Alarm | Standard | DrCmpMinRntime |  | 1x0362 | 1.01 | BI342 | 1.01 | 0 | 1 |  | Drives Compressor: Min Operation Time in Progress: Alarm: Active.
0x1567 | Compressor | Alarm | Standard | DrCmpOvrload |  | 1x0363 | 1.01 | BI343 | 1.01 | 0 | 1 |  | Drives Compressor: Overloaded: Alarm: Active.
0x1568 | Compressor | Alarm | Standard | DrCmpBoostErr |  | 1x0364 | 1.01 | BI344 | 1.01 | 0 | 1 |  | Drives Compressor: Oil Boost Configuration Error: Alarm: Active.
0x11A0 | Compressor | Status | Standard | DCCompLubriact |  | 1x0365 | 1.01 | BI347 | 1.01 | 0 | 1 | 0 | Drives Compressor: Lubrication Operation in Progress: Status: Active
| Filter | Status | Standard | FiltCaliDone_OA |  | 1x0366 | 1.01 | BI353 | 1.01 | 0 | 1 |  | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY
| Filter | Status | Standard | FiltCaliDone_SA |  | 1x0367 | 1.01 | BI354 | 1.01 | 0 | 1 |  | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY
| Filter | Status | Standard | FiltCaliDone_EA1 |  | 1x0368 | 1.01 | BI355 | 1.01 | 0 | 1 |  | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY
| Filter | Status | Standard | FiltCaliDone_EA2 |  | 1x0369 | 1.01 | BI356 | 1.01 | 0 | 1 |  | Filter Calibration done (valid filterpress data) DYNAMICMODE ONLY
0x1F3F | Heat Pump | Alarm | Special | DaikSuctAlr |  | 1x0380 | 1.01 | BI319 | 1.01 | 0 | 1 |  | Special customer code: Daikin EVKit: Suction Temperature: Sensor Alarm: Active.
| Heat Pump | Status | Standard | HP_Stat_Lub |  | 1x0391 | 1.01 | BI350 | 1.10 | 0 | 1 |  | State of the Heat pump Oil/Defrost input
| Heat Exchanger | Alarm | Special | Alr_CF_Timerunout_On |  | 1x0382 | 1.01 | BI352 | 1.10 | 0 | 1 |  | Special customer code: Counterflow Heat exchanger: Deice runs too long time
| Preheater coil | Status | Standard | PH_TempSensErr |  | 1x0370 | 1.01 | BI357 | 1.10 | 0 | 1 |  | Pre-heating coil - Return sensor - Sensor fault
| Compressor | Status | Standard | EXISTS_DV_Compressor |  | 1x0390 | 1.01 | BI358 | 1.10 | 0 | 1 |  | Drive Compressor Existflag
0x1B40 | Fan, Supply | Alarm | Standard | AlrComSupFan |  | 1x0500 | 1.01 | BI185 | 1.01 | 0 | 1 |  | Common Alarm: Supply Air Fan: Alarm: Active.
0x1B41 | Fan, Supply | Alarm | Standard | AlrComSupFlDu |  | 1x0501 | 1.01 | BI187 | 1.01 | 0 | 1 |  | Common Alarm: Supply Air Pressure/Flow: Alarm: Active.
0x1B42 | Fan, Extract | Alarm | Standard | AlrComExtFan |  | 1x0502 | 1.01 | BI186 | 1.01 | 0 | 1 |  | Common Alarm: Extract Air Fan: Alarm: Active.
0x1B43 | Fan, Extract | Alarm | Standard | AlrComExtFlDu |  | 1x0503 | 1.01 | BI188 | 1.01 | 0 | 1 |  | Common Alarm: Extract Air Pressure/Flow: Alarm: Active.
0x1B44 | Heating Coil, Water | Alarm | Standard | AlrComHWPump |  | 1x0504 | 1.01 | BI184 | 1.01 | 0 | 1 |  | Common Alarm: Circulator Pump: Alarm: Active.
0x1B45 | Heat Exchanger | Alarm | Standard | AlrComEXC |  | 1x0505 | 1.01 | BI189 | 1.01 | 0 | 1 |  | Common Alarm: Heat Exchanger: Alarm: Active.
0x1B46 | Heating Coil, Water | Alarm | Standard | AlrComFreeze |  | 1x0506 | 1.01 | BI190 | 1.01 | 0 | 1 |  | Common Alarm: Frost: Alarm: Active.
0x1B47 | Heating Coil, Electric | Alarm | Standard | AlrComElHeat |  | 1x0507 | 1.01 | BI191 | 1.01 | 0 | 1 |  | Common Alarm: Electric Heating Coil: Alarm: Active.
0x1B48 | AHU Controller | Alarm | Standard | AlrComTemp |  | 1x0508 | 1.01 | BI192 | 1.01 | 0 | 1 |  | Common Alarm: Temperature High/Low: Alarm: Active.
0x1B49 | Filter | Alarm | Standard | AlrComSFilt |  | 1x0509 | 1.01 | BI193 | 1.01 | 0 | 1 |  | Common Alarm: Supply Air Filter: Alarm: Active.
0x1B4A | Filter | Alarm | Standard | AlrComEFilt |  | 1x0510 | 1.01 | BI194 | 1.01 | 0 | 1 |  | Common Alarm: Extract Air Filter: Alarm: Active.
0x1B4B | Temp. Sensor | Alarm | Standard | AlrComTmpSens |  | 1x0511 | 1.01 | BI195 | 1.01 | 0 | 1 |  | Common Alarm: Temperature Sensor: Alarm: Active.
0x1B4C | Cooling Coil | Alarm | Standard | AlrComCool |  | 1x0512 | 1.01 | BI196 | 1.01 | 0 | 1 |  | Common Alarm: Cooling: Alarm: Active.
0x1B4D | Damper, Direct Modbus | Alarm | Standard | AlrComBDamp |  | 1x0513 | 1.01 | BI197 | 1.01 | 0 | 1 |  | Common Alarm: Belimo damper: Alarm: Active.
0x1B4E | AHU Controller | Alarm | Standard | AlrComIntern |  | 1x0514 | 1.01 | BI198 | 1.01 | 0 | 1 |  | Common Alarm: Internal Modbus Communicatin Error: Alarm: Active.
0x112D | AHU Controller | Status | Standard | BMS_InpStat |  | 1x0515 | 1.01 | BI199 | 1.01 | 0 | 1 |  | BMS Control: Active.
0x1019 | AHU Controller | Status | Standard | ExternLowState |  | 1x0522 | 1.01 | BI200 | 1.01 | 0 | 1 |  | External Low Speed Input: Active
0x101A | AHU Controller | Status | Standard | StartInpState |  | 1x0523 | 1.01 | BI177 | 1.01 | 0 | 1 |  | External Start Input: Active
| Component | Function | Standard/ Special | Name | SI Unit | Input register (R) (3x) | SW vers. | Analog input (R) (AI) | SW vers. | Min | Max | Factory settings | Comments in English
| Operation mode | Status | Standard | OL_Act_DriftMode |  | 3x0001 | 1.01 | AI0 | 1.01 | 0 | 600 | 0 | Current DriftMode 000-099:Agg Stop, 100-199:Agg Lo Speed, 200-299:Agg Hi Speed, 300-399:Special control modes 410-414:Agg Med Speed
| AHU Controller | Status | Standard | SpecRegModeTx |  | 3x0002 | 1.01 |  | 1.01 | 1 | 1000 |  | Pointer Text Mode web, not in Bacnet
0x2162 | Pressure | Current value | Standard | AR_SupDuctPa | Pa | 3x0003 | 1.01 | AI1 | 1.01 | 0 | 5000 |  | Supply Air Duct: Current Pressure Reading [Pa]
0x2163 | Pressure | Set point | Standard | AR_SupDuctPaRgSet | Pa | 3x0004 | 1.01 | AI2 | 1.01 | 0 | 2000 |  | Supply Air Duct: Pressure SetPoint [Pa]
0x2262 | Pressure | Current value | Standard | AR_ExtDuctPa | Pa | 3x0005 | 1.01 | AI3 | 1.01 | 0 | 5000 |  | Extract Air Duct: Current Pressure Reading [Pa]
0x2263 | Pressure | Set point | Standard | AR_ExtDuctPaRgSet | Pa | 3x0006 | 1.01 | AI4 | 1.01 | 0 | 2000 |  | Extract Air Duct: Pressure SetPoint [Pa]
0x2140 | Fan | Current value | Standard | AR_Act_SA_Flow | l/s | 3x0007 | 1.01 | AI5 | 1.01 | 0 | 30000 |  | Supply Air: Current Flow Reading [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting)
0x2141 | Fan | Set point | Standard | AR_SA_FlowRegSet | l/s | 3x0008 | 1.01 | AI6 | 1.01 | 0 | 30000 |  | Supply Air: Flow SetPoint [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting)
0x2240 | Fan | Current value | Standard | AR_Act_EA_Flow | l/s | 3x0009 | 1.01 | AI7 | 1.01 | 0 | 30000 |  | Extract Air current Flow reading [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting)
0x2241 | Fan | Set point | Standard | AR_EA_FlowRegSet | l/s | 3x0010 | 1.01 | AI8 | 1.01 | 0 | 30000 |  | Extract Air: Flow SetPoint [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting)
0x2450 | CO2 Sensor | Current value | Standard | CO2_ppmMeas | ppm | 3x0011 | 1.01 | AI9 | 1.01 | 0 | 10000 |  | CO2 Sensor , Current Reading [ppm]
0x2441 | Fan | Current value | Standard | FANOpt_SA_Ctrl_Vin | % | 3x0012 | 1.01 | AI101 | 1.01 | 0 | 10000 |  | Supply Fan: Current 0-10 V DC Control Signal
0x2442 | Fan | Current value | Standard | FANOpt_EA_Ctrl_Vin | % | 3x0013 | 1.01 | AI102 | 1.01 | 0 | 10000 |  | Extract Fan: Current 0-10 V DC Control Signal
0x2470 | Fan Optimizer | Current value | Standard | FAN_SupPrcMeas | % | 3x0014 | 1.01 | AI12 | 1.01 | 0 | 10000 |  | Fan Optimizer: Voltage Input: Supply Signal [1/100%]
0x2471 | Fan Optimizer | Current value | Standard | FAN_ExtPrcMeas | % | 3x0015 | 1.01 | AI13 | 1.01 | 0 | 10000 |  | Fan Optimizer: Voltage Input: Extract signal [1/100%]
0x3141 | Fan | Set point | Standard | AR_SA_MaxFlow_AggSize | l/s | 3x0016 | 1.01 | AI14 | 1.01 | 100 | 30000 | 10000 | AHU: Max. Supply Air Flow Capacity [l/s]
0x3241 | Fan | Set point | Standard | AR_EA_MaxFlow_AggSize | l/s | 3x0017 | 1.01 | AI15 | 1.01 | 100 | 30000 | 10000 | AHU: Max. Extract Air Flow Capacity [l/s]
0x2100 | Temp. Supply | Current value | Standard | ATMP_SupTemp | °C | 3x0020 | 1.01 | AI16 | 1.01 | -4000 | 10000 |  | Supply Air Temperature: Current Reading [1/100°C]
0x2101 | Temp. Supply | Set point | Standard | ATMP_SupTempRegSet | °C | 3x0021 | 1.01 | AI17 | 1.01 | -4000 | 7000 |  | Supply Air Temperature: Setpoint [1/100°C] (Including "Temperature Offset" Settings)
0x2200 | Temp. Extract | Current value | Standard | ATMP_ExtTemp | °C | 3x0022 | 1.01 | AI18 | 1.01 | -4000 | 10000 |  | Extract Air Temperature: Current Reading [1/100°C]
0x2201 | Temp. Extract | Set point | Standard | ATMP_ExtTempRegSet | °C | 3x0023 | 1.01 | AI19 | 1.01 | 10 | 6000 |  | Extract Air Temperature: Setpoint [1/100°C] (Including "Temperature Offset" Settings)
0x2300 | Temp. Out door | Current value | Standard | ATMP_Used_OATemp | °C | 3x0024 | 1.01 | AI20 | 1.01 | -6000 | 10000 |  | Outdoor Air temperature: Current Reading [1/100°C]
0x2310 | Temp. Room | Current value | Standard | ATMP_RoomTemp | °C | 3x0025 | 1.01 | AI21 | 1.01 | -4000 | 10000 |  | Room Temperature: Current Reading [1/100°C]
0x2320 | Temp. Exhaust | Current value | Standard | ATMP_ExhaustTemp | °C | 3x0026 | 1.01 | AI22 | 1.01 | -4000 | 10000 |  | Exhaust Air Temperature: Current Reading [1/100°C]
0x2460 | AHU Controller | Current value | Standard | TR_TempRegMeas | °C | 3x0027 | 1.01 | AI23 | 1.01 | -4000 | 10000 |  | Active Temperature Control Loop: Temperature, Current Reading [1/100°C]
0x2461 | AHU Controller | Set point | Standard | TR_TempRegVal | °C | 3x0028 | 1.01 | AI24 | 1.01 | 0 | 4000 |  | Active Temperature Control Loop: Temperature setpoint [1/100°C]
0x2920 | Temp. after Heat Recovery | Current value | Standard | BattEXC_Temp | °C | 3x0029 | 1.01 | AI25 | 1.01 | -4000 | 10000 |  | Water Coil Temperature: Current Reading (Downstream the Heat Exchanger) [1/100°C]
0x2330 | Heating Coil 1, Water | Current value | Standard | ATMP_HW1BattTemp | °C | 3x0030 | 1.01 | AI26 | 1.01 | -4000 | 10000 |  | Heating Coil 1: Return Water Temperature , Current Reading [1/100°C]
0x2121 | Filter | Current value | Standard | FM_SF_OA_ActFiltPress | Pa | 3x0031 | 1.01 | AI27 | 1.01 | 0 | 5000 |  | Outdoor Air Filter: Pressure Drop, Current Reading [Pa]
0x2221 | Filter | Current value | Standard | FM_SF_EA_ActFiltPress | Pa | 3x0032 | 1.01 | AI28 | 1.01 | 0 | 5000 |  | Extract Air Filter: Pressure Drop, Current Reading [Pa]
0x239A | Filter | Average value | Standard | FiltSupFlowAvr | Pa | 3x0033 | 1.01 | AI266 | 1.01 | 0 | 2000 |  | Supply Air Filter: Average Flow - for internal use only in connection to dynamic filter suveilance.
0x2160 | Fan | Set point | Standard | AR_SA_MotorSet | % | 3x0034 | 1.01 | AI29 | 1.01 | 0 | 10000 |  | Supply Air Fan: Setpoint , Current Reading [1/100%]
0x239B | Filter | Average value | Standard | FiltExtFlowAvr | Pa | 3x0035 | 1.01 | AI267 | 1.01 | 0 | 2000 |  | Extract Air Filter: Average Flow - for internal use only in connection to dynamic filter suveilance.
0x2260 | Fan | Set point | Standard | AR_EA_MotorSet | % | 3x0036 | 1.01 | AI30 | 1.01 | 0 | 10000 |  | Extract Air Fan: Setpoint , Current Reading [%]
0x239C | Filter | Average value | Standard | FiltSupPaAvr | Pa | 3x0037 | 1.01 | AI268 | 1.01 | 0 | 3000 |  | Supply Air Filter: Average Pressure Drop Reading [Pa/30]
0x239D | Filter | Average value | Standard | FiltExtPaAvr | Pa | 3x0038 | 1.01 | AI269 | 1.01 | 0 | 3000 |  | Extract Air Filter: Average Pressure Drop Reading [Pa/30]
0x2394 | Filter | Set point | Standard | FiltSupAlrPa | Pa | 3x0039 | 1.01 | AI31 | 1.01 | 0 | 100 |  | Supply Air Filter: Dynamic Alarm Limit, Current Reading [Pa]. ONLY IN DYNAMIC MODE.
0x2395 | Heat Exchanger | Current value | Standard | ATMP_EfficiencyTemp | °C | 3x0040 | 1.01 | AI232 | 1.01 | 0 | 100 |  | Current EfficiencyTemp [1/100C]
0x236C | Temp. heat pump | Current value | Special | HP_OutdCoilTmp | °C | 3x0041 | 1.01 | AI270 | 1.01 | -6000 | 10000 |  | Outdoor Temperature: Current Reading (near Outdoor Heat Pump Parts) [1/100°C]
0x2A84 | Heat Exchanger | Current value | Standard | EXCActualEff | % | 3x0042 | 1.01 | AI108 | 1.01 | 0 | 10000 |  | Heat Exchanger: Efficiency, Current Reading [1/100%]
0x2AF4 | Fan, ATV drive | Current value | Special | AtvSupFCType |  | 3x0043 | 1.01 | AI106 | 1.01 | 0 | 30000 |  | Supply Air Fan: ATV Drive Type - Not in use.
0x2AFC | Fan, ATV drive | Current value | Special | AtvExtFCType |  | 3x0044 | 1.01 | AI107 | 1.01 | 0 | 30000 |  | Exhaust Air Fan: ATV Drive Type - Not in use.
0x239E | Filter | Set point | Standard | FiltSup2AlrPa | Pa | 3x0045 | 1.01 | AI271 | 1.01 | 0 | 100 |  | Outdoor Air Filter: Dynamic Alarm Limit, Current Reading [Pa]. ONLY IN DYNAMIC MODE.
0x239F | Filter | Set point | Standard | FiltExt2AlrPa | Pa | 3x0046 | 1.01 | AI272 | 1.01 | 0 | 100 |  | Extract Air Filter 2: Dynamic Alarm Limit, Current Reading [Pa]. ONLY IN DYNAMIC MODE.
0x2125 | Filter | Average value | Standard | FM_SF_EA2_ActFiltPress | Pa | 3x0047 | 1.01 | AI130 | 1.01 | 0 | 5000 |  | Extract Air Filter 2: Pressure Drop, Current Reading [Pa]
0x2395 | Filter | Set point | Standard | FiltExtAlrPa | Pa | 3x0048 | 1.01 | AI32 | 1.01 | 0 | 100 |  | Extract Air Filter: Dynamic Alarm Limit, Current Reading [Pa]. ONLY IN DYNAMIC MODE.
0x2126 | Filter | Average value | Standard | FM_SF_SA_ActFiltPress | Pa | 3x0049 | 1.01 | AI131 | 1.01 | 0 | 5000 |  | Supply Air Filter: Pressure Drop, Current Reading [Pa]
0x23C0 | AHU Controller | Set point | Standard | AR_FlwTmpCmpOut | % | 3x0050 | 1.01 | AI33 | 1.01 | 0 | 10000 |  | Outdoor Air Temp.: Ventilation Setpoint Compensation, Current Reading [1/100%]
0x2380 | AHU Controller | Summer/Winter comp. | Standard | SWTC_ActSetOfs | C | 3x0051 | 1.01 | AI34 | 1.01 | -1000 | 1000 |  | Summer/Winter: Temperature Setpoint Compensation, Current Reading [1/100°C]
0x2370 | AHU Controller | Summer Night Cooling | Standard | SNC_Heat_On_Time | Sec | 3x0052 | 1.01 | AI273 | 1.01 | 0 | 30000 |  | Summer Night Cooling: Heating Count-up, Current Reading [sec]
0x2400 | Heat exchanger | Set point | Standard | HeatEXCPower | % | 3x0053 | 1.01 | AI35 | 1.01 | 0 | 10000 |  | Heat Exchanger: Setpoint, Current Reading [1/100%]
0x2401 | Heating Coil 1 | Set point | Standard | Heat1Power | % | 3x0054 | 1.01 | AI36 | 1.01 | 0 | 10000 |  | Heating Coil 1: Setpoint, Current Reading [1/100%]
0x2420 | Cooling Coil | Set point | Standard | CoolPower | % | 3x0055 | 1.01 | AI37 | 1.01 | 0 | 10000 |  | Cooling Coil: Setpoint, Current Reading [1/100%]
0x242A | Cooling Coil | Set point | Standard | CoolActPower | % | 3x0056 | 1.01 | AI38 | 1.01 | 0 | 10000 |  | Cooling Coil: Current Reading [1/100%]
0x2421 | Cooling Coil | Set point | Standard | CoolFlwForcePw | % | 3x0057 | 1.01 | AI39 | 1.01 | 0 | 10000 |  | Fan Speed: Forced Cooling Increase, Current Reading [1/100%]
0x2426 | Cooling, DX | Current value | Standard | CL_Cool_Vin1Alarm | % | 3x0058 | 1.01 | AI40 | 1.01 | 0 | 10000 |  | DX Low Pressure 1: Voltage Signal, Current Reading [1/100%]
0x2427 | Cooling, DX | Current value | Standard | CL_Cool_Vin2Alarm | % | 3x0059 | 1.01 | AI41 | 1.01 | 0 | 10000 |  | DX High Pressure 1: Voltage Signal, Current Reading [1/100%]
0x2428 | Cooling, DX | Current value | Standard | CL_Cool_Vin3Alarm | % | 3x0060 | 1.01 | AI42 | 1.01 | 0 | 10000 |  | DX Low Pressure 2: Voltage Signal, Current Reading [1/100%]
0x2429 | Cooling, DX | Current value | Standard | CL_Cool_Vin4Alarm | % | 3x0061 | 1.01 | AI43 | 1.01 | 0 | 10000 |  | DX High Pressure 2: Voltage Signal, Current Reading [1/100%]
0x2500 | Cooling, DX | Current value | Standard | C_LoPress1Bar | Bar | 3x0062 | 1.01 | AI44 | 1.01 | 0 | 10000 |  | DX Low Pressure: Sensor 1, Current Reading [1/100 bar]
0x2501 | Cooling, DX | Current value | Standard | C_HiPress1Bar | Bar | 3x0063 | 1.01 | AI45 | 1.01 | 0 | 10000 |  | DX High Pressure: Sensor 1, Current Reading [1/100 bar]
0x2502 | Cooling, DX | Current value | Standard | C_LoPress2Bar | Bar | 3x0064 | 1.01 | AI46 | 1.01 | 0 | 10000 |  | DX Low Pressure: Sensor 2, Current reading [1/100 bar]
0x2503 | Cooling, DX | Current value | Standard | C_HiPress2Bar | Bar | 3x0065 | 1.01 | AI47 | 1.01 | 0 | 10000 |  | DX High Pressure: Sensor 2, Current Reading [1/100 bar]
0x2408 | Heating Coil 2 | Set point | Standard | Heat2Power | % | 3x0066 | 1.01 | AI103 | 1.01 | 0 | 10000 |  | Heating Coil 2: SetPoint, Current Reading [1/100%]
| Heating Coil 1 | Set point | Standard | HW12_VDCOut | V | 3x0067 | 1.01 | AI380 | 1.01 | 0 | 10000 |  | Heating Coil 1 Out 2: Output Voltage, Current Reading [1/1000V]
0x2A3A | Fan, Supply | Set point | Standard | FCsupMtrPrcSet | % | 3x0077 | 1.01 | AI55 | 1.01 | 0 | 10000 |  | Supply Fan: Setpoint, Current Reading [%]
0x2143 | Fan, Supply | Current value | Standard | AR_SupSFP | J/m | 3x0078 | 1.01 | AI56 | 1.01 | 0 | 10000 |  | Supply Fan: SFP, Current Reading [Ws/m3 same as J/m3]
| Fan, Supply | Current value | Standard | AR_SupSFPII | J/m | 3x0079 | 1.01 | AI251 | 1.01 | 0 | 10000 |  | Supply Fan: SFPII, Current Reading [Ws/m3 same as J/m3]
0x2243 | Fan, Extract | Current value | Standard | AR_ExtSFP | J/m | 3x0088 | 1.01 | AI65 | 1.01 | 0 | 10000 |  | Extract SFP: Current Reading [Ws/m3 same as J/m3]
| Fan, Extract | Current value | Standard | AR_ExtSFPII | J/m | 3x0089 | 1.01 | AI252 | 1.01 | 0 | 10000 |  | Extract SFPII: Current Reading [Ws/m3 same as J/m3]
0x2A70 | Heat Exchanger | Current value | Standard | EXC_Type |  | 3x0090 | 1.01 | AI66 | 1.01 | 0 | 3 |  | Rotary Heat Exchanger: Motor Type.
0x2A71 | Heat Exchanger | SW version | Standard | EXC_Software |  | 3x0091 | 1.01 | AI67 | 1.01 | 0 | 10000 |  | Rotary Heat Exchanger: Software Version [1/100]
0x2A72 | Heat Exchanger | Current value | Standard | EXC_PrcOut | % | 3x0092 | 1.01 | AI68 | 1.01 | 0 | 10000 |  | Rotary Heat Exchanger: Setpoint, Current Reading [1/100%]
0x2A74 | Heat Exchanger | Current value | Standard | EXC_RpmOut | rpm | 3x0093 | 1.01 | AI69 | 1.01 | 0 | 20000 |  | Rotary Heat Exchanger: Speed, Current Reading [1/100 rpm]
0x2A76 | Heat Exchanger | Current value | Standard | EXC_Iout | mA | 3x0094 | 1.01 | AI70 | 1.01 | 0 | 10000 |  | Rotary Heat Exchanger: Current Output, Current reading [mA]
0x2A77 | Heat Exchanger | Current value | Standard | EXC_Power | W | 3x0095 | 1.01 | AI71 | 1.01 | 0 | 100 |  | Rotary Heat Exchanger: Output Power, Current Reading [W]
0x2A79 | Heat Exchanger | Current value | Standard | EXC_DriftDays | Day | 3x0096 | 1.01 | AI72 | 1.01 | 0 | 32000 |  | Rotary Heat Exchanger: Days of Operation, Current Reading
0x2A7A | Heat Exchanger | Set point | Standard | EXC_PrcSet | % | 3x0097 | 1.01 | AI73 | 1.01 | 0 | 10000 |  | Rotary Heat Exchanger: Setpoint, Current Reading [1/100%]
| AHU | SFP High | Standard | AHU_FullSFPHigh | J/m | 3x0098 | 1.01 | AI253 | 1.01 | 0 | 10000 |  | AHU SFP: High [Ws/m3 same as J/m3]
| AHU | SFP Low | Standard | AHU_FullSFPLow | J/m | 3x0099 | 1.01 | AI254 | 1.01 | 0 | 10000 |  | AHU SFP: Low [Ws/m3 same as J/m3]
0x2A90 | IO Extension | SW version | Standard | IO2_ID1_SW_Ver |  | 3x0100 | 1.01 | AI74 | 1.01 | 0 | 10000 |  | Extension Module 1: Software Version [1/100]
0x2AB0 | IO Extension | SW version | Standard | IO2_ID2_SW_Ver |  | 3x0101 | 1.01 | AI75 | 1.01 | 0 | 10000 |  | Extension Module 2: Software Version [1/100]
0x2411 | Preheater Coil | Current value | Standard | ATMP_PHWMTemp | °C | 3x0102 | 1.01 | AI105 | 1.01 | -4000 | 10000 |  | Pre-Heater Coil: Return Water Temperature, Current Reading. [1/100C] Coil/Return
0x2413 | Preheater Coil | Set point | Standard | PH_HeatPower | % | 3x0103 | 1.01 | AI104 | 1.01 | 0 | 10000 |  | Pre-Heater Coil: Setpoint, Current Reading [1/100%]
| Heating Coil, Electric | Status | Special | El_HT1_ActPower |  | 3x0104 | 1.01 | AI226 | 1.01 | 0 | 30000 |  | Special customer code: Electric Heating Coil 1: Power, Current Reading (kW)
| Heating Coil, Electric | Status | Special | El_HT2_ActPower |  | 3x0105 | 1.01 | AI227 | 1.01 | 0 | 30000 |  | Special customer code: Electric Heating Coil 2: Power, Current Reading (kW)
0x2800 | AHU Controller | Time | Standard | RTC_WeekDay |  | 3x0110 | 1.01 | AI76 | 1.01 | 0 | 6 |  | Weekday: Monday..Sunday, Current Reading (1 = Monday, 2 = Tuesday….)
| AHU Controller | Status | Standard | ExtDrfDaysLeft |  | 3x0111 | 1.01 |  | 1.01 | 0 | 6 |  | Extended Drift Day's Left, not on Bacnet
| AHU Controller | Status | Standard | ExtDrfMinLeft |  | 3x0112 | 1.01 |  | 1.01 | 0 | 1439 |  | Extended Drift Minute's Left, not on Bacnet
| Heat Pump | Status | Standard | HP_ExtAirTemp | °C | 3x0113 | 1.01 | AI338 | 1.01 | -5000 | 10000 |  | Extract Air: Temperature after Heat Pump, Current Reading [1/100°C]
0x30E4 | Heat Pump | Current value | Special | DaikSucTmpSet | °C | 3x0114 | 1.01 | AI339 | 1.01 | 0 | 32767 |  | Special customer code: Daikin EVKit: Suction air temperature current reading.
0x236E | Heat Pump | Current value | Standard | HP_CoilPaMeas | Pa | 3x0115 | 1.01 | AI110 | 1.01 | 0 | 5000 |  | Heat Pump: Exhaust Air Coil Pressure Drop, Current Reading
0x2E10 | AHU Controller | Alarm | Standard | Alr_Released00 |  | 3x0120 | 1.01 | AI79 | 1.01 | 0 | 100 |  | Alarms: Stack 00 for Current Active (0 indicates end of stack)
0x2E11 | AHU Controller | Alarm | Standard | Alr_Released01 |  | 3x0121 | 1.01 | AI80 | 1.01 | 0 | 100 |  | Alarms: Stack 01 for Current Active (0 indicates end of stack)
0x2E12 | AHU Controller | Alarm | Standard | Alr_Released02 |  | 3x0122 | 1.01 | AI81 | 1.01 | 0 | 100 |  | Alarms: Stack 02 for Current Active (0 indicates end of stack)
0x2E13 | AHU Controller | Alarm | Standard | Alr_Released03 |  | 3x0123 | 1.01 | AI82 | 1.01 | 0 | 100 |  | Alarms: Stack 03 for Current Active (0 indicates end of stack)
0x2E14 | AHU Controller | Alarm | Standard | Alr_Released04 |  | 3x0124 | 1.01 | AI83 | 1.01 | 0 | 100 |  | Alarms: Stack 04 for Current Active (0 indicates end of stack)
0x2E15 | AHU Controller | Alarm | Standard | Alr_Released05 |  | 3x0125 | 1.01 | AI84 | 1.01 | 0 | 100 |  | Alarms: Stack 05 for Current Active (0 indicates end of stack)
0x2E16 | AHU Controller | Alarm | Standard | Alr_Released06 |  | 3x0126 | 1.01 | AI85 | 1.01 | 0 | 100 |  | Alarms: Stack 06 for Current Active (0 indicates end of stack)
0x2E17 | AHU Controller | Alarm | Standard | Alr_Released07 |  | 3x0127 | 1.01 | AI86 | 1.01 | 0 | 100 |  | Alarms: Stack 07 for Current Active (0 indicates end of stack)
0x2E18 | AHU Controller | Alarm | Standard | Alr_Released08 |  | 3x0128 | 1.01 | AI87 | 1.01 | 0 | 100 |  | Alarms: Stack 08 for Current Active (0 indicates end of stack)
0x2E19 | AHU Controller | Alarm | Standard | Alr_Released09 |  | 3x0129 | 1.01 | AI88 | 1.01 | 0 | 100 |  | Alarms: Stack 09 for Current Active (0 indicates end of stack)
0x2E1A | AHU Controller | Alarm | Standard | Alr_Released10 |  | 3x0130 | 1.01 | AI89 | 1.01 | 0 | 100 |  | Alarms: Stack 10 for Current Active (0 indicates end of stack)
0x2E1B | AHU Controller | Alarm | Standard | Alr_Released11 |  | 3x0131 | 1.01 | AI90 | 1.01 | 0 | 100 |  | Alarms: Stack 11 for Current Active (0 indicates end of stack)
0x2E1C | AHU Controller | Alarm | Standard | Alr_Released12 |  | 3x0132 | 1.01 | AI91 | 1.01 | 0 | 100 |  | Alarms: Stack 12 for Current Active (0 indicates end of stack)
0x2E1D | AHU Controller | Alarm | Standard | Alr_Released13 |  | 3x0133 | 1.01 | AI92 | 1.01 | 0 | 100 |  | Alarms: Stack 13 for Current Active (0 indicates end of stack)
0x2E1E | AHU Controller | Alarm | Standard | Alr_Released14 |  | 3x0134 | 1.01 | AI93 | 1.01 | 0 | 100 |  | Alarms: Stack 14 for Current Active (0 indicates end of stack)
0x2E1F | AHU Controller | Alarm | Standard | Alr_Released15 |  | 3x0135 | 1.01 | AI94 | 1.01 | 0 | 100 |  | Alarms: Stack 15 for Current Active (0 indicates end of stack)
| Humidity | Current value | Standard | Humid_ActRHOut |  | 3x0138 | 1.01 | AI263 | 1.01 | 0 | 100 |  | Outdoor Air: Relative Humidity, Current Reading [%]
| Humidity | Current value | Standard | Humid_ActRHExh |  | 3x0139 | 1.01 | AI264 | 1.01 | 0 | 100 |  | Exhaust Air: Relative Humidity, Current Reading [%]
0x2000 | AHU Controller | SW version | Standard | MasterSW_Ver |  | 3x0140 | 1.01 | AI95 | 1.01 | 0 | 30000 |  | AHU Controller: Software Version [1/100]
0x2001 | HMI Display | SW version | Standard | DisplaySW_Ver |  | 3x0141 | 1.01 | AI96 | 1.01 | 0 | 30000 |  | Touch Panel: Software Version [1/100]
0x2360 | Cooling, DX | Status | Standard | DX_OnTimerRE1 | Sec | 3x0145 | 1.01 | AI274 | 1.01 | 0 | 600 |  | DX Cooling Relay 1: Remaining On Time, Current Reading [sec]
0x2361 | Cooling, DX | Status | Standard | DX_OnTimerRE2 | Sec | 3x0146 | 1.01 | AI275 | 1.01 | 0 | 600 |  | DX Cooling Relay 2: Remaining On Time, Current Reading [sec]
0x2362 | Cooling, DX | Status | Standard | DX_OnTimerRE3 | Sec | 3x0147 | 1.01 | AI276 | 1.01 | 0 | 600 |  | DX Cooling Relay 3: Remaining On Time, Current Reading [sec]
0x2363 | Cooling, DX | Status | Standard | DX_OnTimerRE4 | Sec | 3x0148 | 1.01 | AI277 | 1.01 | 0 | 600 |  | DX Cooling Relay 4: Remaining On Time, Current Reading [sec]
0x2364 | Cooling, DX | Status | Standard | DX_RestartCnt1 |  | 3x0149 | 1.01 | AI278 | 1.01 | 0 | 60 |  | DX Cooling Relay 1: Starts per Hour, Current Reading
0x23A0 | Heating Coil 2, Water | Current value | Standard | HW2BattTemp | °C | 3x0150 | 1.01 | AI279 | 1.01 | -4000 | 10000 |  | Heating Coil 2: Return Water Temperature, Current Reading [1/100°C]
0x2366 | Cooling, DX | Status | Standard | DX_RestartCnt3 |  | 3x0151 | 1.01 | AI280 | 1.01 | 0 | 60 |  | DX Cooling Relay 3: Starts per Hour, Current Reading
0x2367 | Cooling, DX | Status | Standard | DX_RestartCnt4 |  | 3x0152 | 1.01 | AI281 | 1.01 | 0 | 60 |  | DX Cooling Relay 4: Starts per Hour, Current Reading
0x2368 | Cooling, DX | Status | Standard | DX_RestartTim1 | Sec | 3x0153 | 1.01 | AI282 | 1.01 | 0 | 3600 |  | DX Cooling Relay 1: Remaining Off Time, Current Reading [sec]
0x2369 | Cooling, DX | Status | Standard | DX_RestartTim2 | Sec | 3x0154 | 1.01 | AI283 | 1.01 | 0 | 3600 |  | DX Cooling Relay 2: Remaining Off Time, Current Reading [sec]
0x236A | Cooling, DX | Status | Standard | DX_RestartTim3 | Sec | 3x0155 | 1.01 | AI284 | 1.01 | 0 | 3600 |  | DX Cooling Relay 3: Remaining Off Time, Current Reading [sec]
0x236B | Cooling, DX | Status | Standard | DX_RestartTim4 | Sec | 3x0156 | 1.01 | AI285 | 1.01 | 0 | 3600 |  | DX Cooling Relay 4: Remaining Off Time, Current Reading [sec]
0x2390 | Filter | Current value | Standard | FiltSupPrcStat | % | 3x0157 | 1.01 | AI286 | 1.01 | 0 | 10000 |  | Supply Air Filter: Static Alarm Limit [1/100%]
0x2391 | Filter | Current value | Standard | FiltExtPrcStat | % | 3x0158 | 1.01 | AI287 | 1.01 | 0 | 10000 |  | Extract Air Filter: Static Alarm Limit [1/100%]
0x2392 | Filter | Current value | Standard | FiltSupNewPa | Pa | 3x0159 | 1.01 | AI288 | 1.01 | 0 | 100 |  | Supply Air Filter: Pressure at Current Flow (Clean filter), Current Reading [Pa]
0x2393 | Filter | Current value | Standard | FiltExtNewPa | Pa | 3x0160 | 1.01 | AI289 | 1.01 | 0 | 100 |  | Extract Air Filter: Pressure at Current Flow (Clean filter), Current Reading [Pa]
0x2110 | Temp. Sensor | Current value | Standard | AddOnTSensor1 | °C | 3x0161 | 1.01 | AI97 | 1.01 | -4000 | 10000 |  | Temperature Sensor: Add on 1, Current Reading [1/100°C]
0x2111 | Temp. Sensor | Current value | Standard | AddOnTSensor2 | °C | 3x0162 | 1.01 | AI98 | 1.01 | -4000 | 10000 |  | Temperature Sensor: Add on 2, Current Reading [1/100°C]
0x2112 | Temp. Sensor | Current value | Standard | AddOnTSensor3 | °C | 3x0163 | 1.01 | AI99 | 1.01 | -4000 | 10000 |  | Temperature Sensor: Add on 3, Current Reading [1/100°C]
0x2113 | Temp. Sensor | Current value | Standard | AddOnTSensor4 | °C | 3x0164 | 1.01 | AI100 | 1.01 | -4000 | 10000 |  | Temperature Sensor: Add on 4, Current Reading [1/100°C]
0x240F | Cooling, DX | Set point | Special | ROHCondPower | % | 3x0165 | 1.01 | AI290 | 1.01 | 0 | 10000 |  | Special customer code: Condenser Valve: Power Output, Current Reading [1/100%]
0x23AF | Cooling, DX | Set point | Special | ROHCondOutVDC | V | 3x0166 | 1.01 | AI291 | 1.01 | 0 | 10000 |  | Special customer code: Step-up Valve: Voltage, Current Reading. [1/1000 V]
0x240E | Cooling, DX | Set point | Special | ROHShuntPower | % | 3x0167 | 1.01 | AI292 | 1.01 | 0 | 10000 |  | Special customer code: Condenser Coil: Output, Current Reading. [1/100%]
0x23AE | Cooling, DX | Set point | Special | ROHShuntOutVDC | V | 3x0168 | 1.01 | AI293 | 1.01 | 0 | 10000 |  | Special customer code: Shunt Valve: Voltage, Current Reading. [1/1000 V]
0x2479 | Humidity | Set point | Standard | Humid_OutVDC | V | 3x0169 | 1.01 | AI294 | 1.01 | 0 | 10000 |  | Steam Humidifier: Setpoint: Current Reading. [1/1000 V]
0x247A | Humidity | Current value | Standard | Humid_ActRHSup | % | 3x0170 | 1.01 | AI128 | 1.01 | 0 | 10000 |  | Supply Air Duct: Relative Humidity, Current Reading [1/100%rh]
0x247B | Humidity | Current value | Standard | Humid_ActRHExt | % | 3x0171 | 1.01 | AI127 | 1.01 | 0 | 10000 |  | Extract Air Duct: Relative Humidity, Current Reading [1/100%rh]
0x24F1 | Damper, Recirculation | Status | Special | MODREC_AltFlowAct |  | 3x0172 | 1.01 | AI111 | 1.01 | 0 | 2 |  | Special customer code: Recirculation Mode: Alternating Status, Current Reading. 0=No Change; 1=Low to High; 2=High to Low
0x24F2 | Damper, Recirculation | Status | Special | UPS_RecClosTimer | Sec | 3x0173 | 1.01 | AI112 | 1.01 | 0 | 7200 |  | Special customer code: Closed Recirculation: Status Timer, Current Reading [Sec]
0x24F0 | Heating Coil 2 | Status | Special | Ht2DelayTimer | Sec | 3x0174 | 1.01 | AI295 | 1.01 | 0 | 7200 |  | Special customer code: Heating Coil 2: Timer Delay, Current Reading [Sec]
0x2A85 | Heat Exchanger | Current value | Special | REXCPressAvg |  | 3x0175 | 1.01 | AI296 | 1.01 | 0 | 2000 |  | Special customer code: Rotary Heat Exchanger: Exhaust Air Pressure drop, Current Reading [Pa]
0x240A | Combi Coil | Set point | Standard | CombiVDC_Out | V | 3x0176 | 1.01 | AI113 | 1.01 | 0 | 10000 |  | Combi Coil: Control Voltage, Current Reading [1/1000 V]
0x240B | Combi Coil | Set point | Standard | CombiHeatPow | % | 3x0177 | 1.01 | AI114 | 1.01 | 0 | 10000 |  | Combi Coil: SetPoint, Current Reading [1/100 %]
0x240D | Heat Pump | Current value | Standard | HP_HeatPower | % | 3x0178 | 1.01 | AI297 | 1.01 | 0 | 10000 |  | HeatPump: Heating SetPoint, Current Reading (Only active during heating demand. During cooling demand is "CoolPower" " Current Cooling setpoint active")
0x2980 | Fan 2, Supply | Current value | Standard | SA2_Slave_Size |  | 3x0179 | 1.01 | AI298 | 1.01 | 0 | 65535 |  | Supply Air Fan 2: Type
0x2981 | Fan 2, Supply | SW version | Standard | SA2_Slave_MOC_SW_Ver |  | 3x0180 | 1.01 | AI299 | 1.01 | 0 | 10000 |  | Supply Air Fan 2: Software Version [1/100]
0x2982 | Fan 2, Supply | SW version | Standard | SA2_Slave_AOC_SW_Ver |  | 3x0181 | 1.01 | AI300 | 1.01 | 0 | 10000 |  | Supply Air Fan 2: Boot Software / HW Version [1/100]
0x2983 | Fan 2, Supply | Current value | Standard | SA2_Slave_PercentOut | % | 3x0182 | 1.01 | AI301 | 1.01 | 0 | 10000 |  | Supply Air Fan 2: Speed, Current Reading [1/100%]
0x2984 | Fan 2, Supply | Current value | Standard | SA2_Slave_RPM_Out | RPM | 3x0183 | 1.01 | AI302 | 1.01 | 0 | 12000 |  | Supply Air Fan 2: RPM, Current Reading [RPM]
0x2987 | Fan 2, Supply | Current value | Standard | SA2_Slave_I_Out | mA | 3x0184 | 1.01 | AI303 | 1.01 | 0 | 65535 |  | Supply Air Fan 2: Current Output, Current Reading [1/100mA]
0x2988 | Fan 2, Supply | Current value | Standard | SA2_Slave_Power_In | W | 3x0185 | 1.01 | AI304 | 1.01 | 0 | 65535 |  | Supply Air Fan 2: Input Power, Current Reading [Watt]
0x298A | Fan 2, Supply | Current value | Standard | SA2_Slave_DriftMinute | Min | 3x0186 | 1.01 | AI305 | 1.01 | 0 | 1440 |  | Supply Air Fan 2: Operation Time, Current Reading [minutes]
0x298B | Fan 2, Supply | Current value | Standard | SA2_Slave_DriftDays | Day | 3x0187 | 1.01 | AI306 | 1.01 | 0 | 30000 |  | Supply Air Fan 2: Operation Time, Current Reading [days]
0x298C | Fan 2, Supply | Set point | Standard | SA2_Slave_PercentSet | % | 3x0188 | 1.01 | AI307 | 1.01 | 0 | 10000 |  | Supply Air Fan 2: Current setpoint [1/100%]
0x2990 | Fan 2, Extract | Current value | Standard | EA2_Slave_Size |  | 3x0189 | 1.01 | AI308 | 1.01 | 0 | 65535 |  | Extract Air Fan 2: Type
0x2991 | Fan 2, Extract | SW version | Standard | EA2_Slave_MOC_SW_Ver |  | 3x0190 | 1.01 | AI309 | 1.01 | 0 | 10000 |  | Extract Air Fan 2: Software Version [1/100]
0x2992 | Fan 2, Extract | SW version | Standard | EA2_Slave_AOC_SW_Ver |  | 3x0191 | 1.01 | AI310 | 1.01 | 0 | 10000 |  | Extract Air Fan 2: Boot Software / HW Version [1/100]
0x2993 | Fan 2, Extract | Current value | Standard | EA2_Slave_PercentOut | % | 3x0192 | 1.01 | AI311 | 1.01 | 0 | 10000 |  | Extract Air Fan 2: Speed, Current Reading [1/100%]
0x2994 | Fan 2, Extract | Current value | Standard | EA2_Slave_RPM_Out | RPM | 3x0193 | 1.01 | AI312 | 1.01 | 0 | 12000 |  | Extract Air Fan 2: RPM, Current Reading [RPM]
0x2997 | Fan 2, Extract | Current value | Standard | EA2_Slave_I_Out | mA | 3x0194 | 1.01 | AI313 | 1.01 | 0 | 65535 |  | Extract Air Fan 2: Current Output, Current Reading [1/100mA]
0x2998 | Fan 2, Extract | Current value | Standard | EA2_Slave_Power_In | W | 3x0195 | 1.01 | AI314 | 1.01 | 0 | 65535 |  | Extract Air Fan 2; Input Power, Current Reading [Watt]
0x299A | Fan 2, Extract | Current value | Standard | EA2_Slave_DriftMinute | Min | 3x0196 | 1.01 | AI315 | 1.01 | 0 | 1440 |  | Extract Air Fan 2: Operation Time, Current Reading [minutes]
0x299B | Fan 2, Extract | Current value | Standard | EA2_Slave_DriftDays | Day | 3x0197 | 1.01 | AI316 | 1.01 | 0 | 30000 |  | Extract Air Fan 2: Operation Time, Current Reading [days]
0x299C | Fan 2, Extract | Set point | Standard | EA2_Slave_PercentSet | % | 3x0198 | 1.01 | AI317 | 1.01 | 0 | 10000 |  | Extract Air Fan 2: Setpoint, Current Reading [1/100%]
0x247E | Humidity | Current value | Standard | Humid_ActRHMix | % | 3x0199 | 1.01 | AI256 | 1.01 | 0 | 10000 |  | Mixed Air: Relative Humidity, Current Reading [1/100%rh]
0x2960 | Fan, Supply | Current value | Standard | SA_Master_Size |  | 3x0200 | 1.01 | AI318 | 1.01 | 0 | 65535 |  | Supply Air Fan: Type
0x2961 | Fan, Supply | SW version | Standard | SA_Master_MOC_SW_Ver |  | 3x0201 | 1.01 | AI319 | 1.01 | 0 | 1000 |  | Supply Air Fan: Software Version [1/100]
0x2962 | Fan, Supply | SW version | Standard | SA_Master_AOC_SW_Ver |  | 3x0202 | 1.01 | AI320 | 1.01 | 0 | 1000 |  | Supply Air Fan: Boot Software / HW Version [1/100]
0x2963 | Fan, Supply | Current value | Standard | SA_Master_PercentOut | % | 3x0203 | 1.01 | AI321 | 1.01 | 0 | 10000 |  | Supply Air Fan: Speed, Current Reading [1/100%]
0x2964 | Fan, Supply | Current value | Standard | SA_Master_RPM_Out | RPM | 3x0204 | 1.01 | AI322 | 1.01 | 0 | 10000 |  | Supply Air Fan: RPM, Current Reading [RPM]
0x2967 | Fan, Supply | Current value | Standard | SA_Master_I_Out | mA | 3x0205 | 1.01 | AI323 | 1.01 | 0 | 30000 |  | Supply Air Fan: Output Current , Current Reading [1/100mA]
0x2968 | Fan, Supply | Current value | Standard | SA_Master_Power_In | W | 3x0206 | 1.01 | AI365 | 1.01 | 0 | 7000 |  | Supply Air Fan: Input Power, Current Reading [Watt]
0x296A | Fan, Supply | Current value | Standard | SA_Master_DriftMinute | Min | 3x0207 | 1.01 | AI324 | 1.01 | 0 | 1440 |  | Supply Air Fan: Operation Time, Current Reading [minutes]
0x296B | Fan, Supply | Current value | Standard | SA_Master_DriftDays | Day | 3x0208 | 1.01 | AI325 | 1.01 | 0 | 30000 |  | Supply Air Fan: Operation Time, Current Reading [days]
0x296C | Fan, Supply | Set point | Standard | SA_Master_PercentSet | % | 3x0209 | 1.01 | AI326 | 1.01 | 0 | 10000 |  | Supply Air Fan: Setpoint, Current Reading [1/100%]
| Fan, Extract | Current value | Standard | EA_Master_Size |  | 3x0218 | 1.01 | AI334 | 1.01 | 0 | 65535 |  | Extract Air Fan: Type
| Fan, Extract | SW version | Standard | EA_Master_MOC_SW_Ver |  | 3x0219 | 1.01 | AI335 | 1.01 | 0 | 1000 |  | Extract Air Fan: Software Version [1/100]
0x2972 | Fan, Extract | SW version | Standard | EA_Master_AOC_SW_Ver |  | 3x0210 | 1.01 | AI327 | 1.01 | 0 | 1000 |  | Extract Air Fan: Boot Software / HW Version [1/100]
0x2973 | Fan, Extract | Current value | Standard | EA_Master_PercentOut | % | 3x0211 | 1.01 | AI328 | 1.01 | 0 | 10000 |  | Extract Air Fan: Speed, Current Reading [1/100%]
0x2974 | Fan, Extract | Current value | Standard | EA_Master_RPM_Out | RPM | 3x0212 | 1.01 | AI329 | 1.01 | 0 | 10000 |  | Extract Air Fan: RPM, Current Reading [RPM]
0x2977 | Fan, Extract | Current value | Standard | EA_Master_I_Out | mA | 3x0213 | 1.01 | AI330 | 1.01 | 0 | 30000 |  | Extract Air Fan: Current Output, Current Reading [1/100mA]
0x2978 | Fan, Extract | Current value | Standard | EA_Master_Power_In | W | 3x0214 | 1.01 | AI366 | 1.01 | 0 | 7000 |  | Extract Air Fan: Input Power, Current Reading [Watt]
0x297A | Fan, Extract | Current value | Standard | EA_Master_DriftMinute | Min | 3x0215 | 1.01 | AI331 | 1.01 | 0 | 1440 |  | Extract Air Fan: Operation Time, Current Reading [minutes]
0x297B | Fan, Extract | Current value | Standard | EA_Master_DriftDays | Day | 3x0216 | 1.01 | AI332 | 1.01 | 0 | 30000 |  | Extract Air Fan: Operation Time, Current Reading [days]
0x297C | Fan, Extract | Current value | Standard | EA_Master_PercentSet | % | 3x0217 | 1.01 | AI333 | 1.01 | 0 | 10000 |  | Extract Air Fan: Setpoint, Current Reading [1/100%]
0x2104 | Temp. Supply 2 | Current value | Standard | SupplyTemp2 | °C | 3x0220 | 1.01 | AI234 | 1.01 | -4000 | 10000 |  | Special customer code: Supply Air: Temperature 2, Current Reading [1/100°C]
0x2304 | Temp. Out Door | Current value | Standard | ExtOutDTemp | °C | 3x0221 | 1.01 | AI118 | 1.01 | -6000 | 10000 |  | Outdoor Temperature: External Sensor, Current Reading [1/100°C]
0x2410 | Preheater Coil | Current value | Standard | PHeatTempAir | °C | 3x0222 | 1.01 | AI119 | 1.01 | -4000 | 10000 |  | Pre-heated Air: Temperature, Current Reading (Air sensor downstream the pre-heating coil) [1/100°C]
0x2352 | Cooling Coil | Current value | Standard | CW_supplyTemp | °C | 3x0223 | 1.01 | AI120 | 1.01 | -4000 | 10000 |  | Cooling Coil: Water Inlet Temperature, Current Reading [1/100 °C]
0x23D0 | Damper, Recirculation | Status | Standard | RecFreshAirDis | % | 3x0224 | 1.01 | AI121 | 1.01 | 0 | 10000 |  | Outdoor Air / Exhaust Air: Damper Position Setpoint, Current Reading [1/100 %]
0x23D1 | Damper, Recirculation | Status | Standard | RecDampPrcDis | % | 3x0225 | 1.01 | AI122 | 1.01 | 0 | 10000 |  | Recirculaton Damper: Position Setpoint, Current Reading [1/100 %]
0x242C | Cooling Coil | Set point | Standard | CoolVDC_Out2 | V | 3x0226 | 1.01 | AI123 | 1.01 | 0 | 10000 |  | Combi Coil: Output Voltage to Cooling Valve 2, Current Reading [1/1000 V]
| Temp. Out Door | Current value | Standard | OutDoorSenTemp |  | 3x0229 | 1.01 | AI233 | 1.01 | -6000 | 10000 |  | Outdoor Temperature: Sensor, Current Reading [1/100C]
0x2107 | Filter | Status | Standard | OutFilRestDay |  | 3x0230 | 1.01 | AI124 | 1.01 | 0 | 366 |  | Outdoor Air Filter: Remaining Days Until Filter Replacement Alarm, Current Reading.
0x2227 | Filter | Status | Standard | ExtFilRestDay |  | 3x0231 | 1.01 | AI125 | 1.01 | 0 | 366 |  | Extract Air Filter: Remaining Days Until Filter Replacement Alarm, Current Reading.
0x248C | Humidity | Current value | Standard | RelHumMixed | % | 3x0232 | 1.01 | AI129 | 1.01 | 0 | 10000 |  | Mixed Air: Relative Humidity, Current Reading. [1/100%rh]
0x210A | Filter | Status | Standard | SupFi2RestDay |  | 3x0233 | 1.01 | AI336 | 1.01 | 0 | 366 |  | Supply Air Filter: Remaining Days Until Filter Replacement Alarm, Current Reading.
0x222A | Filter | Status | Standard | ExtFil2RestDay |  | 3x0234 | 1.01 | AI337 | 1.01 | 0 | 366 |  | Extract Air Filter 2: Remaining Days Until Filter Replacement Alarm, Current Reading.
0x2600 | Zone | Status | Standard | ZM_Count |  | 3x0235 | 1.01 | AI132 | 1.01 | 0 | 4 |  | Zone Control: Number of Detected Zone Modules.
0x2601 | Zone | Status | Standard | ZM_OpMode |  | 3x0236 | 1.01 | AI133 | 1.01 | 0 | 7 |  | Zone Control: Operation Mode
0x2610 | Zone 1 | Status | Standard | ZM1_Status |  | 3x0237 | 1.01 | AI134 | 1.01 | 0 | 2 |  | Zone Module 1: Status: 0=No Active Alarm; 1=A-Alarm Active; 2=B-Alarm Active
0x2611 | Zone 1 | Status | Standard | ZM1_Sup1Set |  | 3x0238 | 1.01 | AI135 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Supply 1, Actuator Setpoint [scale depending on the connected actuator]
0x2612 | Zone 1 | Status | Standard | ZM1_Sup1Flow |  | 3x0239 | 1.01 | AI136 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Supply 1, Actuator Flow [scale depending on the connected actuator]
0x2613 | Zone 1 | Status | Standard | ZM1_Sup2Set |  | 3x0240 | 1.01 | AI137 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Supply 2, Actuator Setpoint [scale depending on the connected actuator]
0x2614 | Zone 1 | Status | Standard | ZM1_Sup2Flow |  | 3x0241 | 1.01 | AI138 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Supply 2; Actuator Flow [scale depending on the connected actuator]
0x2615 | Zone 1 | Status | Standard | ZM1_ExtSet |  | 3x0242 | 1.01 | AI139 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Extract, Actuator Setpoint [scale depending on the connected actuator]
0x2616 | Zone 1 | Status | Standard | ZM1_ExtFlow |  | 3x0243 | 1.01 | AI140 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Extract, Actuator Flow [scale depending on the connected actuator]
0x2617 | Zone 1 | Status | Standard | ZM1_HeatSet |  | 3x0244 | 1.01 | AI141 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Heating, Actuator Setpoint [scale depending on the connected actuator]
0x2618 | Zone 1 | Status | Standard | ZM1_HeatFlow |  | 3x0245 | 1.01 | AI142 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x2619 | Zone 1 | Status | Standard | ZM1_CoolSet |  | 3x0246 | 1.01 | AI143 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Cooling, Actuator Setpoint [scale depending on the connected actuator]
0x261A | Zone 1 | Status | Standard | ZM1_CoolFlow |  | 3x0247 | 1.01 | AI144 | 1.01 | 0 | 0 |  | Zone Module 1: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x261B | Zone 1 | Status | Standard | ZM1_RoomTemp |  | 3x0248 | 1.01 | AI145 | 1.01 | -4000 | 10000 |  | Zone Module 1: Room Temperature, Value [1/100°C]
0x261C | Zone 1 | Status | Standard | ZM1_SupTemp |  | 3x0249 | 1.01 | AI146 | 1.01 | -4000 | 10000 |  | Zone Module 1: Supply Temperature, Value [1/100°C]
0x261D | Zone 1 | Status | Standard | ZM1_SetOffset |  | 3x0250 | 1.01 | AI147 | 1.01 | -4000 | 10000 |  | Zone Module 1: Remote Setpoint, Offset [1/100°C]
0x261E | Zone 1 | Status | Standard | ZM1_CO2VOC |  | 3x0251 | 1.01 | AI148 | 1.01 | 0 | 5000 |  | Zone Module 1: CO2/VOC, Value [ppm]
0x261F | Zone 1 | Status | Standard | ZM1_RH |  | 3x0252 | 1.01 | AI149 | 1.01 | 0 | 10000 |  | Zone Module 1: RH, Value [1/100%rh]
0x2620 | Zone 2 | Status | Standard | ZM2_Status |  | 3x0253 | 1.01 | AI150 | 1.01 | 0 | 2 |  | Zone Module 2: Status: 0=No Active Alarm; 1=A-Alarm Active; 2=B-Alarm Active
0x2621 | Zone 2 | Status | Standard | ZM2_Sup1Set |  | 3x0254 | 1.01 | AI151 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Supply 1, Actuator Setpoint [scale depending on the connected actuator]
0x2622 | Zone 2 | Status | Standard | ZM2_Sup1Flow |  | 3x0255 | 1.01 | AI152 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Supply 1, Actuator Flow [scale depending on the connected actuator]
0x2623 | Zone 2 | Status | Standard | ZM2_Sup2Set |  | 3x0256 | 1.01 | AI153 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Supply 2, Actuator Setpoint [scale depending on the connected actuator]
0x2624 | Zone 2 | Status | Standard | ZM2_Sup2Flow |  | 3x0257 | 1.01 | AI154 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Supply 2; Actuator Flow [scale depending on the connected actuator]
0x2625 | Zone 2 | Status | Standard | ZM2_ExtSet |  | 3x0258 | 1.01 | AI155 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Extract, Actuator Setpoint [scale depending on the connected actuator]
0x2626 | Zone 2 | Status | Standard | ZM2_ExtFlow |  | 3x0259 | 1.01 | AI156 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Extract, Actuator Flow [scale depending on the connected actuator]
0x2627 | Zone 2 | Status | Standard | ZM2_HeatSet |  | 3x0260 | 1.01 | AI157 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Heating, Actuator Setpoint [scale depending on the connected actuator]
0x2628 | Zone 2 | Status | Standard | ZM2_HeatFlow |  | 3x0261 | 1.01 | AI158 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x2629 | Zone 2 | Status | Standard | ZM2_CoolSet |  | 3x0262 | 1.01 | AI159 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Cooling, Actuator Setpoint [scale depending on the connected actuator]
0x262A | Zone 2 | Status | Standard | ZM2_CoolFlow |  | 3x0263 | 1.01 | AI160 | 1.01 | 0 | 0 |  | Zone Module 2: VAV Cooling, Actuator Flow [scale depending on the connected actuator]
0x262B | Zone 2 | Status | Standard | ZM2_RoomTemp |  | 3x0264 | 1.01 | AI161 | 1.01 | -4000 | 10000 |  | Zone Module 2: Room Temperature, Value [1/100°C]
0x262C | Zone 2 | Status | Standard | ZM2_SupTemp |  | 3x0265 | 1.01 | AI162 | 1.01 | -4000 | 10000 |  | Zone Module 2: Supply Temperature, Value [1/100°C]
0x262D | Zone 2 | Status | Standard | ZM2_SetOffset |  | 3x0266 | 1.01 | AI163 | 1.01 | -4000 | 10000 |  | Zone Module 2: Remote Setpoint, Offset [1/100°C]
0x262E | Zone 2 | Status | Standard | ZM2_CO2VOC |  | 3x0267 | 1.01 | AI164 | 1.01 | 0 | 5000 |  | Zone Module 2: CO2/VOC, Value [ppm]
0x262F | Zone 2 | Status | Standard | ZM2_RH |  | 3x0268 | 1.01 | AI165 | 1.01 | 0 | 10000 |  | Zone Module 2: RH, Value [1/100%rh]
0x2630 | Zone 3 | Status | Standard | ZM3_Status |  | 3x0269 | 1.01 | AI166 | 1.01 | 0 | 2 |  | Zone Module 3: Status: 0=No Active Alarm; 1=A-Alarm Active; 2=B-Alarm Active
0x2631 | Zone 3 | Status | Standard | ZM3_Sup1Set |  | 3x0270 | 1.01 | AI167 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Supply 1, Actuator Setpoint [scale depending on the connected actuator]
0x2632 | Zone 3 | Status | Standard | ZM3_Sup1Flow |  | 3x0271 | 1.01 | AI168 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Supply 1, Actuator Flow [scale depending on the connected actuator]
0x2633 | Zone 3 | Status | Standard | ZM3_Sup2Set |  | 3x0272 | 1.01 | AI169 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Supply 2, Actuator Setpoint [scale depending on the connected actuator]
0x2634 | Zone 3 | Status | Standard | ZM3_Sup2Flow |  | 3x0273 | 1.01 | AI170 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Supply 2; Actuator Flow [scale depending on the connected actuator]
0x2635 | Zone 3 | Status | Standard | ZM3_ExtSet |  | 3x0274 | 1.01 | AI171 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Extract, Actuator Setpoint [scale depending on the connected actuator]
0x2636 | Zone 3 | Status | Standard | ZM3_ExtFlow |  | 3x0275 | 1.01 | AI172 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Extract, Actuator Flow [scale depending on the connected actuator]
0x2637 | Zone 3 | Status | Standard | ZM3_HeatSet |  | 3x0276 | 1.01 | AI173 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Heating, Actuator Setpoint [scale depending on the connected actuator]
0x2638 | Zone 3 | Status | Standard | ZM3_HeatFlow |  | 3x0277 | 1.01 | AI174 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x2639 | Zone 3 | Status | Standard | ZM3_CoolSet |  | 3x0278 | 1.01 | AI175 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Cooling, Actuator Setpoint [scale depending on the connected actuator]
0x263A | Zone 3 | Status | Standard | ZM3_CoolFlow |  | 3x0279 | 1.01 | AI176 | 1.01 | 0 | 0 |  | Zone Module 3: VAV Cooling, Actuator Flow [scale depending on the connected actuator]
0x263B | Zone 3 | Status | Standard | ZM3_RoomTemp |  | 3x0280 | 1.01 | AI177 | 1.01 | -4000 | 10000 |  | Zone Module 3: Room Temperature, Value [1/100°C]
0x263C | Zone 3 | Status | Standard | ZM3_SupTemp |  | 3x0281 | 1.01 | AI178 | 1.01 | -4000 | 10000 |  | Zone Module 3: Supply Temperature, Value [1/100°C]
0x263D | Zone 3 | Status | Standard | ZM3_SetOffset |  | 3x0282 | 1.01 | AI179 | 1.01 | -4000 | 10000 |  | Zone Module 3: Remote Setpoint, Offset [1/100°C]
0x263E | Zone 3 | Status | Standard | ZM3_CO2VOC |  | 3x0283 | 1.01 | AI180 | 1.01 | 0 | 5000 |  | Zone Module 3: CO2/VOC, Value [ppm]
0x263F | Zone 3 | Status | Standard | ZM3_RH |  | 3x0284 | 1.01 | AI181 | 1.01 | 0 | 10000 |  | Zone Module 3: RH, Value [1/100%rh]
0x2640 | Zone 4 | Status | Standard | ZM4_Status |  | 3x0285 | 1.01 | AI182 | 1.01 | 0 | 2 |  | Zone Module 4: Status: 0=No Active Alarm; 1=A-Alarm Active; 2=B-Alarm Active
0x2641 | Zone 4 | Status | Standard | ZM4_Sup1Set |  | 3x0286 | 1.01 | AI183 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Supply 1, Actuator Setpoint [scale depending on the connected actuator]
0x2642 | Zone 4 | Status | Standard | ZM4_Sup1Flow |  | 3x0287 | 1.01 | AI184 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Supply 1, Actuator Flow [scale depending on the connected actuator]
0x2643 | Zone 4 | Status | Standard | ZM4_Sup2Set |  | 3x0288 | 1.01 | AI185 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Supply 2, Actuator Setpoint [scale depending on the connected actuator]
0x2644 | Zone 4 | Status | Standard | ZM4_Sup2Flow |  | 3x0289 | 1.01 | AI186 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Supply 2; Actuator Flow [scale depending on the connected actuator]
0x2645 | Zone 4 | Status | Standard | ZM4_ExtSet |  | 3x0290 | 1.01 | AI187 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Extract, Actuator Setpoint [scale depending on the connected actuator]
0x2646 | Zone 4 | Status | Standard | ZM4_ExtFlow |  | 3x0291 | 1.01 | AI188 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Extract, Actuator Flow [scale depending on the connected actuator]
0x2647 | Zone 4 | Status | Standard | ZM4_HeatSet |  | 3x0292 | 1.01 | AI189 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Heating, Actuator Setpoint [scale depending on the connected actuator]
0x2648 | Zone 4 | Status | Standard | ZM4_HeatFlow |  | 3x0293 | 1.01 | AI190 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x2649 | Zone 4 | Status | Standard | ZM4_CoolSet |  | 3x0294 | 1.01 | AI191 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Cooling, Actuator Setpoint [scale depending on the connected actuator]
0x264A | Zone 4 | Status | Standard | ZM4_CoolFlow |  | 3x0295 | 1.01 | AI192 | 1.01 | 0 | 0 |  | Zone Module 4: VAV Heating, Actuator Flow [scale depending on the connected actuator]
0x264B | Zone 4 | Status | Standard | ZM4_RoomTemp |  | 3x0296 | 1.01 | AI193 | 1.01 | -4000 | 10000 |  | Zone Module 4: Room Temperature, Value [1/100°C]
0x264C | Zone 4 | Status | Standard | ZM4_SupTemp |  | 3x0297 | 1.01 | AI194 | 1.01 | -4000 | 10000 |  | Zone Module 4: Supply Temperature, Value [1/100°C]
0x264D | Zone 4 | Status | Standard | ZM4_SetOffset |  | 3x0298 | 1.01 | AI195 | 1.01 | -4000 | 10000 |  | Zone Module 4: Remote Setpoint, Offset [1/100°C]
0x264E | Zone 4 | Status | Standard | ZM4_CO2VOC |  | 3x0299 | 1.01 | AI196 | 1.01 | 0 | 5000 |  | Zone Module 4: CO2/VOC, Value [ppm]
0x264F | Zone 4 | Status | Standard | ZM4_RH |  | 3x0300 | 1.01 | AI197 | 1.01 | 0 | 10000 |  | Zone Module 4: RH, Value [1/100%rh]
0x20E0 | Energy Meter | Status | Standard | CVMVoltageL1 |  | 3x0301 | 1.01 | AI198 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase L1 to neutral (N) voltage , Current Reading [V]
0x20E1 | Energy Meter | Status | Standard | CVMCurrentL1 |  | 3x0302 | 1.01 | AI199 | 1.01 | 0 | 6000 |  | CVM Energy Meeter: Current L1 value , Current Reading [A]
0x20E2 | Energy Meter | Status | Standard | CVMActPowerL1 |  | 3x0303 | 1.01 | AI200 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power , Current Reading [kW]
0x20E3 | Energy Meter | Status | Standard | CVMVoltageL2 |  | 3x0304 | 1.01 | AI201 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase L2 to neutral (N) voltage , Current Reading [V]
0x20E4 | Energy Meter | Status | Standard | CVMCurrentL2 |  | 3x0305 | 1.01 | AI202 | 1.01 | 0 | 6000 |  | CVM Energy Meeter: Current L2 value , Current Reading [A]
0x20E5 | Energy Meter | Status | Standard | CVMActPowerL2 |  | 3x0306 | 1.01 | AI203 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power , Current Reading [kW]
0x20E6 | Energy Meter | Status | Standard | CVMVoltageL3 |  | 3x0307 | 1.01 | AI204 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase L3 to neutral (N) voltage , Current Reading [V]
0x20E7 | Energy Meter | Status | Standard | CVMCurrentL3 |  | 3x0308 | 1.01 | AI205 | 1.01 | 0 | 6000 |  | CVM Energy Meeter: Current L3 value, Current Reading [A]
0x20E8 | Energy Meter | Status | Standard | CVMActPowerL3 |  | 3x0309 | 1.01 | AI206 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power , Current Reading [kW]
0x20E9 | Energy Meter | Status | Standard | CVMActPowerIII |  | 3x0310 | 1.01 | AI207 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power three phases , Current Reading [W] (Low Byte)
0x20EA | Energy Meter | Status | Standard | CVMFrequency |  | 3x0311 | 1.01 | AI208 | 1.01 | 0 | 600 |  | CVM Energy Meeter: Frequency value , Current Reading [Hz]
0x20EB | Energy Meter | Status | Standard | CVMVoltageL1L2 |  | 3x0312 | 1.01 | AI209 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase-phase Voltage L1 to L2 , Current Reading [V]
0x20EC | Energy Meter | Status | Standard | CVMVoltageL2L3 |  | 3x0313 | 1.01 | AI210 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase-phase Voltage L2 to L3 , Current Reading [V]
0x20ED | Energy Meter | Status | Standard | CVMVoltageL3L1 |  | 3x0314 | 1.01 | AI211 | 1.01 | 0 | 5200 |  | CVM Energy Meeter: Phase-phase Voltage L3 to L1 , Current Reading [V]
0x20EE | Energy Meter | Status | Standard | CVMActEnergIII |  | 3x0315 | 1.01 | AI230 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active energy three phases , Current Reading [kWh]
0x21E1 | Energy Meter | Status | Standard | CVMCurrentL1H |  | 3x0316 | 1.01 | AI235 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21E2 | Energy Meter | Status | Standard | CVMActPowerL1H |  | 3x0317 | 1.01 | AI236 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power [W] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21E4 | Energy Meter | Status | Standard | CVMCurrentL2H |  | 3x0318 | 1.01 | AI237 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21E5 | Energy Meter | Status | Standard | CVMActPowerL2H |  | 3x0319 | 1.01 | AI238 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power [W] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21E7 | Energy Meter | Status | Standard | CVMCurrentL3H |  | 3x0320 | 1.01 | AI239 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21E8 | Energy Meter | Status | Standard | CVMActPowerL3H |  | 3x0321 | 1.01 | AI240 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power [W] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0X21E9 | Energy Meter | Status | Standard | CVMActPoweIIIH |  | 3x0322 | 1.01 | AI241 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active power three phases [W] (High Byte) Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21EE | Energy Meter | Status | Standard | CVMActEnerIIIH |  | 3x0323 | 1.01 | AI242 | 1.01 | 0 | 65535 |  | CVM Energy Meeter: Active energy three phases [Wh] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x20F0 | Energy Meter | Status | Standard | CCVMVoltageL1 |  | 3x0330 | 1.01 | AI212 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase L1 to neutral (N) voltage , Current Reading [V]
0x20F1 | Energy Meter | Status | Standard | CCVMCurrentL1 |  | 3x0331 | 1.01 | AI213 | 1.01 | 0 | 6000 |  | CCVM Energy Meeter: Cool Current L1 value , Current Reading [A]
0x20F2 | Energy Meter | Status | Standard | CCVMActPowerL1 |  | 3x0332 | 1.01 | AI214 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Cool Active power , Current Reading [kW]
0x20F3 | Energy Meter | Status | Standard | CCVMVoltageL2 |  | 3x0333 | 1.01 | AI215 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase L2 to neutral (N) voltage , Current Reading [V]
0x20F4 | Energy Meter | Status | Standard | CCVMCurrentL2 |  | 3x0334 | 1.01 | AI216 | 1.01 | 0 | 6000 |  | CVM Energy Meeter: Cool Current L2 value , Current Reading [A]
0x20F5 | Energy Meter | Status | Standard | CCVMActPowerL2 |  | 3x0335 | 1.01 | AI217 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Cool Active power , Current Reading [kW]
0x20F6 | Energy Meter | Status | Standard | CCVMVoltageL3 |  | 3x0336 | 1.01 | AI218 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase L3 to neutral (N) voltage , Current Reading [V]
0x20F7 | Energy Meter | Status | Standard | CCVMCurrentL3 |  | 3x0337 | 1.01 | AI219 | 1.01 | 0 | 6000 |  | CCVM Energy Meeter: Cool Current L3 value , Current Reading [A]
0x20F8 | Energy Meter | Status | Standard | CCVMActPowerL3 |  | 3x0338 | 1.01 | AI220 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Cool Active power , Current Reading [kW]
0x20F9 | Energy Meter | Status | Standard | CCVMActPowrIII |  | 3x0339 | 1.01 | AI221 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Cool Active power three phases , Current Reading [W] (Low Byte)
0x20FA | Energy Meter | Status | Standard | CCVMFrequency |  | 3x0340 | 1.01 | AI222 | 1.01 | 0 | 600 |  | CCVM Energy Meeter: Cool Frequency value , Current Reading [Hz]
0x20FB | Energy Meter | Status | Standard | CCVMVoltagL1L2 |  | 3x0341 | 1.01 | AI223 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase-phase Voltage L1 to L2 , Current Reading [V]
0x20FC | Energy Meter | Status | Standard | CCVMVoltagL2L3 |  | 3x0342 | 1.01 | AI224 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase-phase Voltage L2 to L3 , Current Reading [V]
0x20FD | Energy Meter | Status | Standard | CCVMVoltagL3L1 |  | 3x0343 | 1.01 | AI225 | 1.01 | 0 | 5200 |  | CCVM Energy Meeter: Cool Phase-phase Voltage L3 to L1 , Current Reading [V]
0x20FE | Energy Meter | Status | Standard | CCVMActEnergIII |  | 3x0344 | 1.01 | AI231 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Cool Active energy three phases , Current Reading [kWh]
0x21F1 | Energy Meter | Status | Standard | CCVMCurrentL1H |  | 3x0345 | 1.01 | AI243 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21F2 | Energy Meter | Status | Standard | CCVMActPoweL1H |  | 3x0346 | 1.01 | AI244 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Active power [W] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21F4 | Energy Meter | Status | Standard | CCVMCurrentL2H |  | 3x0347 | 1.01 | AI245 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21F5 | Energy Meter | Status | Standard | CCVMActPoweL2H |  | 3x0348 | 1.01 | AI246 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Active power [W] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21F7 | Energy Meter | Status | Standard | CCVMCurrentL3H |  | 3x0349 | 1.01 | AI247 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Current value [mA] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21F8 | Energy Meter | Status | Standard | CCVMActPoweL3H |  | 3x0350 | 1.01 | AI248 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Active power [W] - Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0X21F9 | Energy Meter | Status | Standard | CCVMActPowIIIH |  | 3x0351 | 1.01 | AI249 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Active power three phases [W] (High Byte) Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x21FE | Energy Meter | Status | Standard | CCVMActEnrIIIH |  | 3x0352 | 1.01 | AI347 | 1.01 | 0 | 65535 |  | CCVM Energy Meeter: Active energy three phases [Wh] Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| Energy Meter | Status | Standard | CCVMConActEner3PhkWHH |  | 3x0353 | 1.01 | AI355 | 1.01 | 0 | 65535 |  | Consumed kWh High Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| Energy Meter | Status | Standard | CCVMConActEner3PhkWH |  | 3x0354 | 1.01 | AI356 | 1.01 | 0 | 65535 |  | Consumed kWh Low Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| Energy Meter | Status | Standard | CCVMConActEner3PhWHH |  | 3x0355 | 1.01 | AI357 | 1.01 | 0 | 65535 |  | Consumed Wh High Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
| Energy Meter | Status | Standard | CCVMConActEner3PhWH |  | 3x0356 | 1.01 | AI358 | 1.01 | 0 | 65535 |  | Consumed Wh Low Note!: Values are calculated as (High byte) x 65536 + (Low byte) - High and low bytes = Integer
0x2C70 | Compressor | Status | Standard | DC_Compressor_DriveType |  | 3x0370 | 1.01 | AI255 | 1.01 | 1000 | 65535 | 0 | Drives Compressor: Drive Type
0x2C71 | Compressor | Status | Standard | DC_Compressor_AOCSWVer |  | 3x0371 | 1.01 | AI341 | 1.01 | 0 | 65535 | 0 | Drives Compressor: AOC SW version
0x2C72 | Compressor | Status | Standard | DC_Compressor_MOCSWVer |  | 3x0372 | 1.01 | AI342 | 1.01 | 0 | 65535 | 0 | Drives Compressor: MOC SW version
0x2C73 | Compressor | Status | Standard | DC_Compressor_PercentOut |  | 3x0373 | 1.01 | AI343 | 1.01 | 0 | 10000 | 0 | Drives Compressor: Setpoint , Current Reading
0x2C74 | Compressor | Status | Standard | DC_Compressor_RPM_Out |  | 3x0374 | 1.01 | AI344 | 1.01 | 0 | 3000 | 0 | Drives Compressor: RPM , Current Reading
0x2C78 | Compressor | Status | Standard | DCompPowerIn |  | 3x0378 | 1.01 | AI345 | 1.01 | 0 | 20000 | 0 | Drives Compressor: Input Power , Current Reading
0x2C7B | Compressor | Status | Standard | DCompOpDays |  | 3x0381 | 1.01 | AI346 | 1.01 | 0 | 9999 | 0 | Drives Compressor: Operation days , Current Reading
| Cross EXC | Value | Standard | EXC_FlwAvr |  | 3x0382 | 1.01 | AI348 | 1.01 | 0 | 30000 | 0 | Cross-EXC pressure average depent on flow
0x2B70 | Damper | Status | Standard | BDInletSetPrc |  | 3x0450 | 1.01 | AI450 | 1.01 | 0 | 10000 |  | Outdoor Air Damper: Setpoint, Current Reading [%]
0x2B71 | Damper | Status | Standard | BDInletRelPos | % | 3x0451 | 1.01 | AI451 | 1.01 | 0 | 10000 |  | Outdoor Air Damper: Position , Current Reading [%]
0x2C31 | Damper | Status | Standard | BDExhauSetPrc |  | 3x0452 | 1.01 | AI452 | 1.01 | 0 | 10000 |  | Exhaust Air Damper: Setpoint, Current Reading [%]
0x2B72 | Damper | Status | Standard | BDExhauRelPos | % | 3x0453 | 1.01 | AI453 | 1.01 | 0 | 10000 |  | Exhaust Air Damper: Position , Current Reading [%]
0x2B73 | Damper | Status | Standard | BDExhBakSetPrc |  | 3x0454 | 1.01 | AI454 | 1.01 | 0 | 10000 |  | Exhaust Air Backup Damper: Setpoint, Current Reading [%]
0x2B74 | Damper | Status | Standard | BDExhBakRelPos | % | 3x0455 | 1.01 | AI455 | 1.01 | 0 | 10000 |  | Exhaust Air back up: Damper: Position, Current Reading [%]
0x2B75 | Damper | Status | Standard | BDRecSetPrc |  | 3x0456 | 1.01 | AI456 | 1.01 | 0 | 10000 |  | Recirculation Air Damper: Setpoint, Current Reading [%]
0x2C3C | Damper | Status | Standard | BDRecRelPos | % | 3x0457 | 1.01 | AI457 | 1.01 | 0 | 10000 |  | Recirculation Air Damper: Position, Current Reading [%]
0x2B76 | Damper | Status | Standard | BDByPasSetPrc |  | 3x0458 | 1.01 | AI458 | 1.01 | 0 | 10000 |  | Heat Recovery By-Pass Damper: Setpoint, Current Reading [%]
0x2B77 | Damper | Status | Standard | BDByPasRelPos | % | 3x0459 | 1.01 | AI459 | 1.01 | 0 | 10000 |  | Heat Recovery By-Pass Damper: Position, Current Reading [%]
0x2B78 | Damper | Status | Standard | BDDryinSetPrc |  | 3x0460 | 1.01 | AI460 | 1.01 | 0 | 10000 |  | Filter Drying Damper: Setpoint, Current Reading [%]
0x2B79 | Damper | Status | Standard | BDDryinRelPos | % | 3x0461 | 1.01 | AI461 | 1.01 | 0 | 10000 |  | Drying Damper: Position, Current Reading [%]
0x2B7A | Damper | Status | Standard | BDSASetPrc |  | 3x0462 | 1.01 | AI462 | 1.01 | 0 | 10000 |  | Supply Air Damper: Setpoint, Current Reading [%]
0x2B7B | Damper | Status | Standard | BDSuppRelPos | % | 3x0463 | 1.01 | AI463 | 1.01 | 0 | 10000 |  | Supply Air Damper: Position, Current Reading [%]
0x2B7C | Damper | Status | Standard | BDSupBakSetPrc |  | 3x0464 | 1.01 | AI464 | 1.01 | 0 | 10000 |  | Supply Air Backup Damper: Setpoint, Current Reading [%]
0x2B7D | Damper | Status | Standard | BDSupBakRelPos | % | 3x0465 | 1.01 | AI465 | 1.01 | 0 | 10000 |  | Supply Air Back Up Damper: Position, Current Reading [%]
0x2B7E | Damper | Status | Special | BDSmokeSetPrc |  | 3x0466 | 1.01 | AI466 | 1.01 | 0 | 10000 |  | Special customer code: Smoke Evacuation Damper: Setpoint, Current Reading [%]
0x2B7F | Damper | Status | Special | BDSmokeRelPos | % | 3x0467 | 1.01 | AI467 | 1.01 | 0 | 10000 |  | Special customer code: Smoke Evacuation Damper: Position, Current Reading [%]
| Damper | Status | Special | BDSMBPSetPrc |  | 3x0468 | 1.01 | AI468 | 1.01 | 0 | 10000 |  | Special customer code: Smoke ByPass Damper: Setpoint, Current Reading [%]
| Damper | Status | Special | BDSMBPRelPos | % | 3x0469 | 1.01 | AI469 | 1.01 | 0 | 10000 |  | Special customer code: Smoke ByPass Damper: Position, Current Reading [%]
| Valve | Status | Standard | BVHeat1SetPrc |  | 3x0470 | 1.01 | AI470 | 1.01 | 0 | 10000 |  | Heating Coil 1 Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVHeat1RelPos | % | 3x0471 | 1.01 | AI471 | 1.01 | 0 | 10000 |  | Heating Coil 1 Valve: Position, Current Reading [%]
| Valve | Status | Standard | BVCoolSetPrc |  | 3x0472 | 1.01 | AI472 | 1.01 | 0 | 10000 |  | Cooling Coil 1 Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVCoolRelPos | % | 3x0473 | 1.01 | AI473 | 1.01 | 0 | 10000 |  | Cooling Coil 1 Valve Position, Current Reading [%]
| Valve | Status | Standard | BVHeat2SetPrc |  | 3x0474 | 1.01 | AI474 | 1.01 | 0 | 10000 |  | Heating Coil 2 Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVHeat2RelPos | % | 3x0475 | 1.01 | AI475 | 1.01 | 0 | 10000 |  | Heating Coil 2 Valve: Position, Current Reading [%]
| Valve | Status | Standard | BVFlExcSetPrc |  | 3x0476 | 1.01 | AI476 | 1.01 | 0 | 10000 |  | Run Around Coil Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVFlExcRelPos | % | 3x0477 | 1.01 | AI477 | 1.01 | 0 | 10000 |  | Run Around Coil Valve: Position, Current Reading [%]
| Valve | Status | Standard | BVPrHeatSetPrc |  | 3x0478 | 1.01 | AI478 | 1.01 | 0 | 10000 |  | PreHeater Coil Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVPrHeatRelPos | % | 3x0479 | 1.01 | AI479 | 1.01 | 0 | 10000 |  | PreHeater Coil Valve: Postion, Current Reading [%]
| Valve | Status | Standard | BVCombSetPrc |  | 3x0480 | 1.01 | AI480 | 1.01 | 0 | 10000 |  | Combi Coil Valve: Setpoint, Current Reading [%]
| Valve | Status | Standard | BVCombRelPos | % | 3x0481 | 1.01 | AI481 | 1.01 | 0 | 10000 |  | Combi Coil Valve: Postion, Current Reading [%]
| Valve | Status | Standard | BVOpt7RelPos | % | 3x0483 | 1.01 | AI483 | 1.01 | 0 | 10000 |  | Not used yet.
| Damper | Status | Standard | BDExtSetPrc |  | 3x0484 | 1.01 | AI484 | 1.01 | 0 | 10000 |  | Extract Air Damper: Setpoint, Current Reading [%]
| Valve | Status | Standard | BDExtRelPos | % | 3x0485 | 1.01 | AI485 | 1.01 | 0 | 10000 |  | Extract Air Damper: Position, Current Reading [%]
| Scheduler | Status | Standard | SO_ES_1_MaxStartDate |  | 3x0500 | 1.01 | AI370 | 1.01 | 0 | 34 |  | Exception 1: MaxStartDate
| Scheduler | Status | Standard | SO_ES_1_MaxStartDate |  | 3x0501 | 1.01 | AI371 | 1.01 | 0 | 34 |  | Exception 2: MaxStartDate
| Scheduler | Status | Standard | SO_ES_1_MaxStartDate |  | 3x0502 | 1.01 | AI372 | 1.01 | 0 | 34 |  | Exception 3: MaxStartDate
| Scheduler | Status | Standard | SO_ES_PresentValue_1 |  | 3x0503 | 1.01 | AI373 | 1.01 | 0 | 1 |  | Scheduler Object Execption 1: Present value
| Scheduler | Status | Standard | SO_ES_PresentValue_2 |  | 3x0504 | 1.01 | AI374 | 1.01 | 0 | 1 |  | Scheduler Object Execption 2: Present value
| Scheduler | Status | Standard | SO_ES_PresentValue_3 |  | 3x0505 | 1.01 | AI375 | 1.01 | 0 | 1 |  | Scheduler Object Execption 3: Present value
| Scheduler | Status | Standard | SO_PresentValue |  | 3x0506 | 1.01 | AI376 | 1.01 | 0 | 5 |  | 0-N.U., 1-Stop all, 2-Low, 3-Med, 4-High, 5-_ExtStopScheduler
| Scheduler | Status | Standard | CO_PresentValue_1 |  | 3x0507 | 1.01 | AI377 | 1.01 | 0 | 1 |  | Calendar Object: Present value 1
| Scheduler | Status | Standard | CO_PresentValue_2 |  | 3x0508 | 1.01 | AI378 | 1.01 | 0 | 1 |  | Calendar Object: Present value 2
| Scheduler | Status | Standard | CO_PresentValue_3 |  | 3x0509 | 1.01 | AI379 | 1.01 | 0 | 1 |  | Calendar Object: Present value 3
| Component | Function | Standard/ Special | Name | SI Unit | Holding register (R/W) (4x) | SW vers. | Analog value (R/W) (AV) | SW vers. | Min | Max | Factory settings | Comments in English
| AHU Controller | Set point |  | OL_Manual_Modes |  | 4x0001 |  | AV1 |  | 0 | 6 | 1 | Set AHU operation mode: 1-ManStop, 2-ManLo, 3- ManMed, 4-ManHi, 6-AdvScheduler. Don't set it to 0.
0x3440 | AHU Controller | Set point |  | AR_MtrRegMode |  | 4x0002 |  | AV2 |  | 0 | 12 | 0 | Set Fan reguation: 0=pressure 1=flow 2=extract slave 3=supply slave 4=external V DC setpoint 5=Fan Optimizer supply/extract 6=Fan Optimizer with extract slave 7-Green Zone 8-Green Zone slave 9-Constant speed
0x3270 | AHU Controller | Set point | Special | STMP_NightSetBack | °C | 4x0013 |  | AV306 |  | 0 | 2000 | 0 | Special customer code: "Low speed reduced duty" temperature setpoint reduction Setpoin[1/100°C]
0x3441 | Fan | Set point | Standard | AR_MtrRegOffset | % | 4x0017 |  | AV14 |  | -5000 | 5000 | 0 | Supply/extract Fan offset Setpoint [1/100%]. Active in Slave Fan regulation modes and Constant CO2/VOC
0x346E | Fan | Set point | Standard | AR_CO2_MinPerc | % | 4x0018 |  | AV320 |  | 1000 | 5000 | 1000 | Constant CO2 Fan regulation: Min. Fan % Setpoint [1/100%] (Active if Fan Airflow not is measured)
0x346F | Fan | Set point | Standard | AR_CO2_MaxPerc | % | 4x0019 |  | AV321 |  | 1000 | 10000 | 8000 | Constant CO2 Fan regulation: Max. Fan % Setpoint [1/100%] (Active if Fan Airflow not is measured)
0x3456 | CO2 Sensor | Set point | Standard | AR_CO2_MinFlow | l/s | 4x0022 |  | AV19 |  | 0 | 30000 | 3000 | Constant CO2 Fan regulation: Min. flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting in the AHU Controller)
0x3457 | CO2 Sensor | Set point | Standard | AR_CO2_MaxFlow | l/s | 4x0023 |  | AV20 |  | 0 | 30000 | 7000 | Constant CO2 Fan regulation: Max. flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending on the engineering unit setting in the AHU Controller)
0x3458 | CO2 Sensor | Set point | Standard | AR_CO2_SupFlwOffs | % | 4x0024 |  | AV21 |  | -5000 | 5000 | 0 | Constant CO2 Fan regulation: Supply flow offset Setpoint [1/100%]
0x3453 | CO2 Sensor | Alarm | Standard | AR_CO2_AlrLimit | ppm | 4x0025 |  | AV22 |  | 100 | 10000 | 2000 | Constant CO2 Fan regulation: CO2 alarm limit Setpoint [ppm]
0x3454 | CO2 Sensor | Control | Standard | AR_CO2_PB | ppm | 4x0026 |  | AV23 |  | 10 | 10000 | 500 | Constant CO2 Fan regulation: P-band Setpoint [ppm]
0x3455 | CO2 Sensor | Control | Standard | AR_CO2_I_Time | sec | 4x0027 |  | AV24 |  | 10 | 30000 | 700 | Constant CO2 Fan regulation: I-time [sec]
0x3470 | Fan Optimizer | Set point | Standard | FANOpt_SA_MinFlow | l/s | 4x0028 |  | AV25 |  | 0 | 30000 | 2000 | Fan Optimizer Fan regulation: Min. Supply Air flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending on engineering unit setting in the AHU Controller)
0x3471 | Fan Optimizer | Set point | Standard | FANOpt_SA_MaxFlow | l/s | 4x0029 |  | AV26 |  | 0 | 30000 | 10000 | Fan Optimizer Fan regulation: Min. Extract Air flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending on tengineering unit setting in the AHU Controller)
0x3472 | Fan Optimizer | Set point | Standard | FANOpt_EA_MinFlow | l/s | 4x0030 |  | AV27 |  | 0 | 30000 | 2000 | Fan Optimizer Fan regulation: Max. Supply Air flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending on engineering unit setting in the AHU Controller)
0x3473 | Fan Optimizer | Set point | Standard | FANOpt_EA_MaxFlow | l/s | 4x0031 |  | AV28 |  | 0 | 30000 | 10000 | Fan Optimizer Fan regulation: Max. Extract Air flow Setpoint. [l/s] or [m3/h] or [CFM] (Depending onengineering unit setting in the AHU Controller)
0x3474 | Fan Optimizer | Set point | Standard | FANOpt_EA_FlwOffs | % | 4x0032 |  | AV29 |  | -5000 | 5000 | 0 | Fan Optimizer Fan regulation: Extract Air flow offset setpoint [1/100%]
0x3143 | Fan | Control | Standard | AR_SupMtr_I_Time | sec | 4x0033 |  | AV30 |  | 5 | 1000 | 50 | Supply Fan control: I-time setpoint [sec]
0x3243 | Fan | Control | Standard | AR_ExtMtr_I_Time | sec | 4x0034 |  | AV31 |  | 5 | 1000 | 50 | Extract Fan control: I-time setpoint [sec]
0x3122 | Fan | Fire | Special | AH_SA_FlowFireSet | % | 4x0035 |  | AV32 |  | 0 | 10000 | 8000 | Supply Fan Fire alarm speed setpoint [%]
0x3222 | Fan | Fire | Special | AH_EA_FlowFireSet | % | 4x0036 |  | AV33 |  | 0 | 10000 | 8000 | Extract Fan Fire alarm speed setpoint [%]
0x3001 | Fan | Control | Special | OL_HS_AfterRun_SetTimer |  | 4x0037 |  | AV34 |  | 0 | 480 | 0 | Set Run-on time on external high input [min]
0x33C0 | Fan | Set point | Special | AR_FlwTmpCmpSet | % | 4x0040 |  | AV35 |  | 0 | 5000 | 2500 | Set outdoor air temperature compensation of ventilation: Max. compensation [1/100%]
0x33C1 | Fan | Set point | Special | AR_FlwTmpCmpStart | °C | 4x0041 |  | AV36 |  | -1000 | 1500 | 500 | Set outdoor air temperature compensation of ventilation: Min. Outdoor temp. setpoint [1/100°C]
0x33C2 | Fan | Set point | Special | AR_FlwTmpCmpStop | °C | 4x0042 |  | AV37 |  | -3000 | -1000 | -2000 | Set outdoor air temperature compensation of ventilation: Max. Outdoor temp. setpoint [1/100°C]
0x3347 | Cooling, DX | Set point | Special | DXOutTempMin1 | °C | 4x0043 |  | AV211 |  | 0 | 4000 | 1600 | Set Min. outdoor temperature for activation of DX relay no. 1
0x3348 | Cooling, DX | Set point | Special | DXOutTempMin2 | °C | 4x0044 |  | AV212 |  | 0 | 4000 | 1600 | Set Min. outdoor temperature for activation of DX relay no. 2
0x3349 | Cooling, DX | Set point | Special | DXOutTempMin3 | °C | 4x0045 |  | AV213 |  | 0 | 4000 | 1600 | Set Min. outdoor temperature for activation of DX relay no. 3
0x334A | Cooling, DX | Set point | Special | DXOutTempMin4 | °C | 4x0046 |  | AV214 |  | 0 | 4000 | 1600 | Set Min. outdoor temperature for activation of DX relay no. 4
0x3800 | AHU Controller | Time | Standard | RTC_Year_Uset |  | 4x0050 |  | AV38 |  | 2000 | 2099 |  | Current Year
0x3801 | AHU Controller | Time | Standard | RTC_Month_Uset |  | 4x0051 |  | AV39 |  | 1 | 12 |  | Current Month
0x3802 | AHU Controller | Time | Standard | RTC_Date_Uset |  | 4x0052 |  | AV40 |  | 1 | 31 |  | Current Date
0x3803 | AHU Controller | Time | Standard | RTC_Hour_Uset | h | 4x0053 |  | AV41 |  | 0 | 23 |  | Current Hour
0x3804 | AHU Controller | Time | Standard | RTC_Minute_Uset | Min | 4x0054 |  | AV42 |  | 0 | 59 |  | Current Minutes
0x3805 | AHU Controller | Time | Standard | RTC_Second_Uset | Sec | 4x0055 |  | AV43 |  | 0 | 59 |  | Current Seconds
0x3808 | AHU Controller | Control | Standard | ExtDrfStartDay |  | 4x0056 |  | AV44 |  | 0 | 6 | 0 | Boost start – Day (0=Mon..6=Sun)
0x3809 | AHU Controller | Control | Standard | ExtDrfStartMin | Min | 4x0057 |  | AV45 |  | 0 | 1439 | 0 | Boost start – Time (hours times 60 plus minutes)
0x380A | AHU Controller | Control | Standard | ExtDrfStopDay |  | 4x0058 |  | AV46 |  | 0 | 6 | 0 | Boost stop – Day (0=Mon..6=Sun)
0x380B | AHU Controller | Control | Standard | ExtDrfStopMin | Min | 4x0059 |  | AV47 |  | 0 | 1439 | 0 | Boost stop – Time (hours times 60 plus minutes)
| AHU Controller | Control | Standard | AR_SA_DuctPaLoSet | Pa | 4x0060 |  | AV50 |  | 0 | 5000 | 50 | Supply Air Duct: Low Speed Pressure Setpoint [Pa]
| AHU Controller | Control | Standard | AR_SA_DuctPaHiSet | Pa | 4x0062 |  | AV52 |  | 0 | 5000 | 200 | Supply Air Duct: High Speed Duct Pressure Setpoint [Pa]
| AHU Controller | Control | Standard | AR_EA_DuctPaLoSet | Pa | 4x0063 |  | AV53 |  | 0 | 5000 | 50 | Extract Air Duct: Low Speed Pressure Setpoint [Pa]
| AHU Controller | Control | Standard | AR_EA_DuctPaMedSet | Pa | 4x0064 |  | AV54 |  | 0 | 5000 | 120 | Extract Air Duct: Medium Speed Pressure Setpoint [Pa]
| AHU Controller | Control | Standard | AR_EA_DuctPaHiSet | Pa | 4x0065 |  | AV55 |  | 0 | 5000 | 200 | Extract Air Duct: High Speed Duct Pressure Setpoint [Pa]
| AHU Controller | Control | Standard | AR_SA_LoSpeedFlowSet | l/s | 4x0066 |  | AV56 |  | 0 | 30000 | 1500 | Supply Air Duct: Low Speed Flow Setpoint [l/s]
| AHU Controller | Control | Standard | AR_SA_HiSpeedFlowSet | l/s | 4x0068 |  | AV58 |  | 0 | 30000 | 5000 | Supply Air Duct: High Speed Flow Setpoint [l/s]
| AHU Controller | Control | Standard | AR_EA_LoSpeedFlowSet | l/s | 4x0069 |  | AV59 |  | 0 | 30000 | 1500 | Extract Air Duct: Low Speed Flow Setpoint [l/s]
| AHU Controller | Control | Standard | AR_EA_MedSpeedFlowSet | l/s | 4x0070 |  | AV60 |  | 0 | 30000 | 3000 | Extract Air Duct: Medium Speed Flow Setpoint [l/s]
| AHU Controller | Control | Standard | AR_EA_HiSpeedFlowSet | l/s | 4x0071 |  | AV61 |  | 0 | 30000 | 5000 | Extract Air Duct: High Speed Flow Setpoint [l/s]
| AHU Controller | Control | Standard | AR_SA_FixLoPrcSet | % | 4x0072 |  | AV62 |  | 100 | 10000 | 2500 | Supply Air Fan: Low Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_SA_FixMedPrcSet | % | 4x0073 |  | AV63 |  | 100 | 10000 | 3500 | Supply Air Fan: Medium Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_SA_FixHiPrcSet | % | 4x0074 |  | AV64 |  | 100 | 10000 | 5000 | Supply Air Fan: High Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_EA_FixLoPrcSet | % | 4x0075 |  | AV65 |  | 100 | 10000 | 2500 | Extract Air Fan: Low Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_EA_FixMedPrcSet | % | 4x0076 |  | AV66 |  | 100 | 10000 | 3500 | Extract Air Fan: Medium Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_EA_FixHiPrcSet | % | 4x0077 |  | AV67 |  | 100 | 10000 | 5000 | Extract Air Fan: High Speed Motor Setpoint [1/100%]
| AHU Controller | Control | Standard | AR_CO2_UsetLP | ppm | 4x0078 |  | AV68 |  | 0 | 10000 | 1000 | Constant CO2 Fan regulation: Low Speed CO2 Setpoint [ppm]
| AHU Controller | Control | Standard | AR_CO2_UsetMP | ppm | 4x0079 |  | AV69 |  | 0 | 10000 | 850 | Constant CO2 Fan regulation: Medium Speed CO2 Setpoint [ppm]
| AHU Controller | Control | Standard | AR_CO2_UsetHP | ppm | 4x0080 |  | AV70 |  | 0 | 10000 | 750 | Constant CO2 Fan regulation: High Speed CO2 Setpoint [ppm]
| AHU Controller | Control | Standard | AR_EA_DuctMinFlowSet | l/s | 4x0081 |  | AV71 |  | 0 | 30000 | 1500 | Extract Air Duct: Min. Airflow Setpoint [l/s]
0x3826 | AHU Controller | Control | Standard | AR_EA_DuctMaxFlowSet | l/s | 4x0082 |  | AV72 |  | 0 | 30000 | 10000 | Extract Air Duct: Max Airflow Setpoint [l/s]
0x3827 | AHU Controller | Control | Standard | AR_SA_DuctMinFlowSet | l/s | 4x0083 |  | AV73 |  | 0 | 30000 | 1500 | Supply Air Duct: Min. Airflow Setpoint [l/s]
0x3828 | AHU Controller | Control | Standard | AR_SA_DuctMaxFlowSet | l/s | 4x0084 |  | AV74 |  | 0 | 30000 | 10000 | Supply Air Duct: Max. Airflow Setpoint [l/s]
| AHU Controller | Control | Standard | SupTempDif2Alr | K | 4x0085 |  | AV75 |  | 0 | 3000 | 1000 | TempDiff2 between Set/Meas Alarm Limit SA [1/100C], Preheater only
| AHU Controller | Control | Standard | SupTempDiffAlr | K | 4x0086 |  | AV76 |  | 200 | 1500 | 500 | TempDiff between Set/Meas Alarm Limit SA [1/100C], Afterheat EA/RM
| AHU Controller | Control | Standard | SupTempHeatPB | K | 4x0087 |  | AV77 |  | 200 | 10000 | 750 | P-Band for Supply TempReg heating [1/100C]
| Temp. Out door | Set point | Standard | TR_AlrLimOA_MBT_Min | °C | 4x0116 |  | AV104 |  | -6000 | 0 |  | Modbus Outdoor temperature sensor: Min. temperature Alarm limit setpoint. [1/100°C]
| Temp. Out door | Set point | Standard | TR_AlrLimOA_MBT_Max | °C | 4x0117 |  | AV105 |  | 0 | 6000 |  | Modbus Outdoor temperature sensor: Max. temperature Alarm limit setpoint. [1/100°C]
| Temp. Room | Set point | Standard | TR_AlrLimRoomMin | °C | 4x0118 |  | AV106 |  | -1000 | 1500 |  | Modbus Room temperature sensor: Min. temperature Alarm limit setpoint. [1/100°C]
0x3849 | Temp. Room | Set point | Standard | TR_AlrLimRoomMax | °C | 4x0119 |  | AV107 |  | 0 | 4000 |  | Modbus Room temperature sensor: Max. temperature Alarm limit setpoint. [1/100°C]
0x3460 | AHU Controller | Control | Standard | AHU_TempRegMode |  | 4x0148 |  | AV133 |  | 0 | 3 | 0 | Set Temperature regulation mode: 0= Constant Supply air, 1= Constant Extract air, 2= Constant Room, 3= Supply Air slave.
0x3461 | AHU Controller | Set point | Standard | TR_TempRegSet | °C | 4x0149 |  | AV134 |  | 0 | 4000 |  | Temperature setpoint for current regulation mode [1/100°C]
0x3101 | AHU Controller | Set point | Standard | STMP_SupTempMinSet | °C | 4x0150 |  | AV135 |  | 0 | 4000 | 1000 | Min. Supply Air temperature limit Setpoint [1/100°C]
0x3102 | AHU Controller | Set point | Standard | STMP_SupTempMaxSet | °C | 4x0151 |  | AV136 |  | 2000 | 5000 | 3500 | Max. Supply Air temperature limit Setpoint [1/100°C]
0x3103 | AHU Controller | Set point | Standard | STMP_SupTempDiffSet | °C | 4x0152 |  | AV137 |  | 100 | 1500 | 300 | Supply Air Offset temperature Setpoint [1/100°C]. Only active in Temperature regulation mode 3= Supply Air slave.
0x3111 | Cooling Coil | Control | Standard | TR_SupTempCool_IT | sec | 4x0158 |  | AV140 |  | 10 | 30000 | 700 | Set I-time for Supply Air Cooling Coil control [sec]
0x3112 | Heat exchanger | Control | Standard | TR_SupTempEXC_IT | sec | 4x0159 |  | AV141 |  | 10 | 30000 | 120 | Set I-time for Supply Air heat exchanger control [sec]
0x3113 | Heating | Control | Standard | TR_SupTempHeat_IT | sec | 4x0160 |  | AV142 |  | 10 | 30000 | 300 | Set I-time for Supply Air heating coil control [sec]
0x3114 | Fan | Control | Standard | TR_SupTempDnRegIt | sec | 4x0161 |  | AV143 |  | 10 | 30000 | 120 | Set I-time for Supply Air flow reduction in case of low Supply Air temperature [sec]
0x3105 | Heater 2 | Control | Standard | TR_SupTempHeat2IT | sec | 4x0088 |  | AV78 |  | 10 | 30000 | 300 | Set I-time for Supply Air heating 2 coil control [sec]
0x3109 | Heat pump | Control | Speciel | TR_SupTempHP_IT | sec | 4x0089 |  | AV79 |  | 10 | 30000 | 300 | Set I-time for Supply Air Heat Pump control [sec]
0x3208 | Heating | Alarm |  | STMP_ExtTempDiffAlr | °C | 4x0165 |  | AV144 |  | 200 | 1500 | 500 | Set Extract Air temperature Alarm limit [1/100°C]. Alarm limit is relative to current Extract Air setpoint.
0x3210 | Heating | Control |  | ExtTempHeatPB | °C | 4x0166 |  | AV145 |  | 200 | 10000 | 500 | Set P-band for Extract Air temperature control [1/100°C]
0x3211 | Cooling Coil | Control | Standard | TR_ExtTempCool_It | sec | 4x0167 |  | AV146 |  | 10 | 30000 | 1000 | Set I-time for Extract Air Cooling Coil control [sec]
0x3212 | Heat Exchanger | Control | Standard | TR_ExtTempEXC_It | sec | 4x0168 |  | AV147 |  | 10 | 30000 | 300 | Set I-time for Extract Air heat exchanger control [sec]
0x3213 | Heating | Control | Standard | TR_ExtTempHeat_It | sec | 4x0169 |  | AV148 |  | 10 | 30000 | 600 | Set I-time for Extract Air heating coil control [sec]
0x3214 | Fan | Control | Standard | TR_ExtTempDnRegIt | sec | 4x0170 |  | AV149 |  | 10 | 30000 | 300 | Set I-time for Extract Air flow reduction in case of low Supply Air temperature [sec]
0x3215 | Heater 2 | Control | Standard | ExtTempHeat2It | sec | 4x0090 |  | AV80 |  | 10 | 30000 | 600 | Set I-time for heating 2 coil control [sec]
0x3209 | Heat Pump | Control | Standard | ExtTempHP_IT | sec | 4x0091 |  | AV81 |  | 10 | 30000 | 600 | Set I-time for Extract Air Heatpump control [sec]
0x3380 | AHU Controller | Summer/Winter comp. | Standard | SWTC_WintX1 | °C | 4x0175 |  | AV150 |  | -3000 | 0 | -1500 | Summer/winter temp. comp.: Low Outdoor temp. setpoint, winter [1/100°C]
0x3381 | AHU Controller | Summer/Winter comp. | Standard | SWTC_WintX2 | °C | 4x0176 |  | AV151 |  | -1000 | 1000 | 0 | Summer/winter temp. comp.: High Outdoor temp. setpoint, winter [1/100°C]
0x3382 | AHU Controller | Summer/Winter comp. | Standard | SWTC_SumX1 | °C | 4x0177 |  | AV152 |  | 1000 | 3000 | 2000 | Summer/winter temp. comp.: Low Outdoor temp. setpoint, summer [1/100°C]
0x3383 | AHU Controller | Summer/Winter comp. | Standard | SWTC_SumX2 | °C | 4x0178 |  | AV153 |  | 2000 | 4000 | 3000 | Summer/winter temp. comp.: High Outdoor temp. setpoint, summer [1/100°C]
0x3384 | AHU Controller | Summer/Winter comp. | Standard | SWTCWinComVal | °C | 4x0179 |  | AV154 |  | 0 | 1000 | 500 | Summer/winter temp. comp.: Winter Compensation setpoint [1/100°C]
0x3385 | AHU Controller | Summer/Winter comp. | Standard | SWTCSumComVal | °C | 4x0180 |  | AV155 |  | -1000 | 1000 | -500 | Summer/winter temp. comp.: Summer Compensation setpoint [1/100°C]
0x3510 | Cooling Coil | Alarm | Standard | CL_LoPress1Alr | Bar | 4x0181 |  | AV315 |  | 0 | 10000 | 300 | DX coil: Low Pressure Sensor 1 Alarm Limit setpoint [1/100 Bar]
0x3511 | Cooling Coil | Alarm | Standard | CL_HiPress1Alr | Bar | 4x0182 |  | AV316 |  | 0 | 10000 | 1500 | DX coil: High Pressure Sensor 1 Alarm Limit setpoint [1/100 Bar]
0x3512 | Cooling Coil | Alarm | Standard | CL_LoPress2Alr | Bar | 4x0183 |  | AV317 |  | 0 | 10000 | 300 | DX coil: Low Pressure Sensor 2 Alarm Limit setpoint [1/100 Bar]
0x3513 | Cooling Coil | Alarm | Standard | CL_HiPress2Alr | Bar | 4x0184 |  | AV318 |  | 0 | 10000 | 1500 | DX coil: High Pressure Sensor 2 Alarm Limit setpoint [1/100 Bar]
0x33D0 | AHU Controller | Summer/Winter comp. | Standard | SW_Mode |  | 4x0185 |  | AV156 |  | 0 | 4 | 0 | Set Summer/Winter changeover: 0 = OFF (no Summer/Winter changeover) 1 = Changeover based on Outdoor temperature 2 = Changeover on specific Dates 3 = Constant Summer 4 = Constant Winter
0x33D1 | AHU Controller | Summer/Winter comp. | Standard | SW_OutWinterON | °C | 4x0186 |  | AV157 |  | -3000 | 4000 | 0 | Outdoor Temperature setpoint for start of Winter operation (Changeover = 1) [1/100°C]
0x33D2 | AHU Controller | Summer/Winter comp. | Standard | SW_OutSummerON | °C | 4x0187 |  | AV158 |  | -3000 | 4000 | 2000 | Outdoor Temperature setpoint for start of Summer operation (Changeover = 1) [1/100°C]
0x33D3 | AHU Controller | Summer/Winter comp. | Standard | SW_MonthWintON |  | 4x0188 |  | AV159 |  | 7 | 12 | 11 | Set Calender Month for start of Winter operation (Changeover = 2)
0x33D4 | AHU Controller | Summer/Winter comp. | Standard | SW_DateWintON |  | 4x0189 |  | AV160 |  | 1 | 31 | 1 | Set Date for start of Winter operation (Changeover = 2)
0x33D5 | AHU Controller | Summer/Winter comp. | Standard | SW_MonthSumON |  | 4x0190 |  | AV161 |  | 1 | 6 | 5 | Set Calender Month for start of Summer operation (Changeover = 2)
0x33D6 | AHU Controller | Summer/Winter comp. | Standard | SW_DateSumON |  | 4x0191 |  | AV162 |  | 1 | 31 | 1 | Set Date for start of Summer operation (Changeover = 2)
0x33E0 | Damper, Recirculation | Set point | Standard | NH_Recirce_StartTmp | °C | 4x0195 |  | AV163 |  | 500 | 4000 | 1900 | Night Heat: Startup Room Temperature setpoint [1/100 °C]
0x33E1 | Damper, Recirculation | Set point | Standard | NH_Recirce_StopTmp | °C | 4x0196 |  | AV164 |  | 500 | 4000 | 2100 | Night Heat: Stop Room Temperature setpoint [1/100 °C]
0x33E4 | Damper, Recirculation | Set point | Special | NH_Recirce_StartTmp2 | °C | 4x0197 |  | AV295 |  | 500 | 5000 | 1900 | Recirculation: Start Room Temperature setpoint ROH below 5 deg [1/100 C]
0x33E5 | Damper, Recirculation | Set point | Special | NH_Recirce_StopTmp2 | °C | 4x0198 |  | AV296 |  | 500 | 5000 | 2100 | Recirculation: Stop Room Temperature setpoint ROH below 5 deg [1/100 C]
0x33E6 | Damper, Recirculation | Set point | Standard | NH_Recirce_SwitchTmp2 | °C | 4x0199 |  | AV297 |  | 0 | 5000 | 500 | Recirculation: heat switch Temperature setpoint ROH [1/100 C]
0x3104 | AHU Controller | Fire |  | AH_SA_Temp_InternFireAlr | °C | 4x0200 |  | AV165 |  | 5000 | 12000 | 8000 | Internal Fire Alarm: Supply Air Temperature Setpoint [1/100C]
0x3204 | AHU Controller | Fire |  | AH_EA_Temp_InternFireAlr | °C | 4x0201 |  | AV166 |  | 3500 | 12000 | 7000 | Internal Fire Alarm: Extract Air Temperature Setpoint [1/100C]
0x3420 | Cooling Coil | Control | Standard | CL_Cool_FlwForcePc | % | 4x0205 |  | AV167 |  | 0 | 10000 | 2500 | Forced Cooling Speed increase Setpoint [1/100 %]
0x3421 | Cooling Coil | Set point | Standard | CL_Cool_OutTmpMin | °C | 4x0206 |  | AV168 |  | 0 | 3000 | 1500 | Cooling: Outdoor Temperature 1 stop setpoint . Active cooling is blocked below setpoint.
0x3422 | Cooling Coil | Set point | Standard | CL_Cool_SupMinTmp | °C | 4x0207 |  | AV169 |  | 0 | 2500 | 1200 | Cooling: Min Supply Air Temperature setpoint during active cooling
0x3370 | AHU Controller | Summer Night Cooling | Standard | SNC_EATempStart | °C | 4x0210 |  | AV170 |  | 1500 | 4000 | 2300 | Summer Night Cooling: Max. Room temperature setpoint [1/100°C] (Start)
0x3371 | AHU Controller | Summer Night Cooling | Standard | SNC_EA_TempStop | °C | 4x0211 |  | AV171 |  | 1000 | 3000 | 2000 | Summer Night Cooling: Min. Room temperature setpoint [1/100°C] (Stop)
0x3372 | AHU Controller | Summer Night Cooling | Standard | SNC_OA_TempStart | °C | 4x0212 |  | AV172 |  | 500 | 2000 | 1200 | Summer Night Cooling: Min. Outdoor temperature setpoint [1/100°C] (Start blocked below)
0x3373 | AHU Controller | Summer Night Cooling | Standard | SNC_SA_TempSet | °C | 4x0213 |  | AV173 |  | 500 | 2000 | 1000 | Summer Night Cooling: Min Supply Air tempeperature setpoint [1/100°C]
0x3374 | AHU Controller | Summer Night Cooling | Standard | SNC_StartTime | Min | 4x0214 |  | AV174 |  | 0 | 1439 | 1380 | Summer Night Cooling: Start time setpoint [min]
0x3375 | AHU Controller | Summer Night Cooling | Standard | SNC_StopTime | Min | 4x0215 |  | AV175 |  | 0 | 1439 | 360 | Summer Night Cooling: Stop time setpoint [min]
0x3320 | Heat Exchanger | Set point | Special | CExcDeIceTemp | °C | 4x0220 |  | AV176 |  | -500 | 2000 | 500 | Counterflow Heat Exchanger: Min. Exhaust Air temperature setpoint [1/100°C]
0x3321 | Heat Exchanger | Control | Special | CExcDeIceTempP | °C | 4x0221 |  | AV177 |  | 200 | 2000 | 500 | Counterflow Heat Exchanger: Set P-band for bypass ice protection control [1/100°C]
0x3323 | Heat Exchanger | Set point | Special | CExcDeIcePress | Pa | 4x0222 |  | AV313 |  | 10 | 5000 | 30 | Counterflow Heat Exchanger: Counterflow Heat Exchanger de-icing Pressure drop setpoint [Pa]
0x3324 | Heat Exchanger | Control | Special | CExcDeIceTime | Sec | 4x0223 |  | AV314 |  | 180 | 1800 | 300 | Counterflow Heat Exchanger: De-icing duration setpoint [sec]
0x3920 | Heat Exchanger | Control | Standard | BattEXC_PumpFc |  | 4x0225 |  | AV178 |  | 0 | 3 | 1 | Set Run Around Coil Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when heat recovery is required. 2 = Outdoor Air temp: The Circulator Pump starts at low Outdoor temperatures.
0x3921 | Heat Exchanger | Control | Standard | BattEXC_PumpSt | °C | 4x0226 |  | AV179 |  | 0 | 4000 | 1500 | Run Around Coil : Outdoor temperature setpoint for start of Circulator Pump. [1/100°C]
0x3922 | Heat Exchanger | Alarm | Standard | BattEXC_AlrSet | °C | 4x0227 |  | AV180 |  | -1000 | 2000 | 800 | Run Around Coil: Temperature Alarm setpoint [1/100°C]. The alarm is active if the Return Water temperature is below setpoint + the current Outdoor Temperature.
0x3478 | Humidity | Set point | Standard | Humid_SupSet | % | 4x0228 |  | AV082 |  | 0 | 10000 | 2000 | Humidity setpoint for active Humidity control loop [1/100%] RH. (Supply Air or Extract Air humidity)
0x3330 | Heating coil 1, Water | Set point | Standard | HW1_UpStartPow | % | 4x0230 |  | AV181 |  | 0 | 10000 | 5000 | Water Heating coil 1: Valve setpoint during AHU start up. [1/100%]
0x3331 | Heating Coil 1, Water | Control | Standard | HW1_PumpFunc |  | 4x0231 |  | AV182 |  | 0 | 3 | 1 | Set Water Heating Coil 1 Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when active heating is required. 2 = Outdoor Air temp: The Circulator Pump starts at low Outdoor temperatures.
0x3332 | Heating Coil 1, Water | Set point | Standard | HW1_PmpStartTmp | °C | 4x0232 |  | AV183 |  | 500 | 3000 | 1500 | Water Heating Coil 1: Outdoor temperature setpoint for start of Circulator Pump. [1/100°C].
0x3333 | Heating Coil 1, Water | Set point | Standard | HW1_FrzStopSet | °C | 4x0233 |  | AV184 |  | 500 | 4000 | 2500 | Water Heating Coil 1: Frost protection Return Water temperature Setpoint during AHU stop [1/100°C]
0x3334 | Heating Coil 1, Water | Set point | Standard | HW1_FrzDriftSet | °C | 4x0234 |  | AV185 |  | 200 | 2000 | 500 | Water Heating Coil 1: Frost protection Return Water temperature Setpoint during AHU operation [1/100°C]
0x3335 | Heating Coil 1, Water | Control | Standard | HW1FreezePB | °C | 4x0235 |  | AV186 |  | 200 | 2000 | 500 | Water Heating Coil 1: Frost protection P-band setpoint [1/100°C]
0x3336 | Heating Coil 1, Water | Set point | Standard | HW1_FrzAlrTpSet | °C | 4x0236 |  | AV187 |  | 200 | 2000 | 200 | Water Heating Coil 1: Frost protection Return water temperature alarm setpoint [1/100°C]
0x333C | Heating Coil 1, Water | Set point | Standard | HW1_PmpStartPrc | % | 4x0237 |  | AV312 |  | 0 | 10000 | 300 | Water Heating Coil 1: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x3350 | Cooling Coil | Control | Standard | CW_PumpFunc |  | 4x0240 |  | AV188 |  | 0 | 3 | 0 | Set Water Cooling Coil Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when active cooling is required. 2 = Outdoor Air temp: The Circulator Pump starts at high Outdoor temperatures.
0x3351 | Cooling Coil | Set point | Standard | CW_PmpStartTmp | °C | 4x0241 |  | AV189 |  | 500 | 4000 | 2100 | CoolWaterBatt PumpStartTemp. Is used together with WaterPumpFunc = 2. Pump = ON when OutDoorTemp > PumpStartTemp
0x3475 | GreenZone | Set point | Standard | FANOpt_SA_GZ_An_In | % | 4x0242 |  | AV223 |  | 0 | 10000 |  | GreenZone Fan Regulation: Supply Air setpoint [1/100%]
0x3476 | GreenZone | Set point | Standard | FANOpt_EA_GZ_An_In | % | 4x0243 |  | AV224 |  | 0 | 10000 |  | GreenZone Fan Regulation: Extract Air setpoint [1/100%]
0x3390 | Filter | Alarm | Standard | FiltSupStatAlr | Pa | 4x0245 |  | AV190 |  | 10 | 500 | 80 | Supply Air Filter: Pressure drop Alarm Limit setpoint (static pressure)
0x3391 | Filter | Alarm | Standard | FiltExtStatAlr | Pa | 4x0246 |  | AV191 |  | 10 | 500 | 80 | Extract Air Filter: Pressure drop Alarm Limit setpoint (static pressure)
0x3392 | Filter | Alarm | Standard | FiltSupDynAlr | % | 4x0247 |  | AV192 |  | 1000 | 10000 | 5000 | Supply Air Filter: Pressure drop Alarm Limit Setpoint (dynamic pressure) [1/100%]
0x3393 | Filter | Alarm | Standard | FiltExtDynAlr | % | 4x0248 |  | AV193 |  | 1000 | 10000 | 5000 | Extract Air Filter: Pressure drop Alarm Limit setpiont (dynamic pressure) [1/100%]
0x339B | Filter | Alarm | Standard | FiltSup2StaAlr | Pa | 4x0249 |  | AV258 |  | 10 | 500 | 80 | Supply Air Filter2: Pressure drop Alarm Limit setpoint (static pressure)
0x3E07 | AHU Controller | Alarm | Standard | Alr_MailSetup |  | 4x0250 |  | AV194 |  | 0 | 3 | 3 | Set Alarm email notifications 0 = Emails not sent 1 = Emails sent for A-alarms 2 = Emails sent for B-alarms 3 = Emails sent for A and B-alarms
0x3005 | AHU Controller | Alarm | Standard | AHU_UserAlr_RE_Func |  | 4x0251 |  | AV195 |  | 0 | 4 | 0 | Set User Relasy (B-Alarm relay) Function: 0 = B-alarm 1 = Follow Low speed 2 = Follow High speed 3 = Follow SumNight cooling/ Free cooling 4 = Follow Medium speed
0x34C5 | Preheater Coil | Set point | Standard | PH_StartPrc | % | 4x0252 |  | AV206 |  | 0 | 30000 | 5000 | Water Pre-heating Coil: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x34CC | Preheater Coil | Control | Standard | PHPumpMode |  | 4x0253 |  | AV210 |  | 0 | 4 | 0 | Set Water Pre-heating Coil Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when active heating is required. 2 = Outdoor Air temp: The Circulator Pump starts at low Outdoor temperatur
0x34CB | Preheater Coil | Set point | Standard | STMP_PHPmpStTmpH | °C | 4x0254 |  | AV208 |  | 500 | 3000 | 1000 | Water Pre-heating Coil: Outdoor temperature setpoint for start of Circulator Pump. [1/100°C].
0x34C4 | Preheater Coil | Set point | Standard | PH_StandbyTmp | °C | 4x0255 |  | AV205 |  | 500 | 4000 | 2500 | Water Pre-heating Coil: Frost protection Return Water temperature Setpoint during AHU stop [1/100°C]
0x34CE | Preheater Coil | Set point | Standard | STMP_PHFrzDrSetH | °C | 4x0256 |  | AV209 |  | 200 | 2000 | 500 | Water Pre-heating Coil: Frost protection Return Water temperature Setpoint during AHU operation [1/100°C]
0x34C8 | Preheater Coil | Control | Standard | PHeatFrzPB | °C | 4x0257 |  | AV207 |  | 200 | 2000 | 500 | Water Pre-heating Coil: Frost protection P-band setpoint [1/100°C]
0x34C3 | Preheater Coil | Alarm | Standard | PH_MinAlrFrz | °C | 4x0258 |  | AV204 |  | -4000 | 10000 | 200 | Water Pre-heating Coil: Frost protection Return water temperature alarm setpoint [1/100°C]
0x34C2 | Preheater Coil | Set point | Standard | PH_HeatSet | °C | 4x0259 |  | AV203 |  | -3000 | 2000 | 200 | Pre-heating Coil: Supply Air Duct Pre-heater temperature Setpoint.
0x3400 | Heating Coil 2, Water | Set point | Standard | HW2UpStartPow | % | 4x0260 |  | AV196 |  | 0 | 10000 | 5000 | Water Heating coil 2: Valve setpoint during AHU start up. [1/100%]
0x3401 | Heating Coil 2, Water | Control | Standard | HW2PumpFunc |  | 4x0261 |  | AV197 |  | 0 | 3 | 1 | Set Water Heating Coil 2 Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when active heating is required. 2 = Outdoor Air temp: The Circulator Pump starts at low Outdoor temperatur
0x3402 | Heating Coil 2, Water | Set point | Standard | HW2PmpStartTmp | °C | 4x0262 |  | AV198 |  | 500 | 3000 | 1500 | Water Heating Coil 2: Outdoor temperature setpoint for start of Circulator Pump. [1/100°C].
0x340C | Heating Coil 2, Water | Set point | Standard | HW2PmpStartPrc | % | 4x0263 |  | AV311 |  | 0 | 10000 | 300 | Water Heating Coil 2: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x3403 | Heating Coil 2, Water | Set point | Standard | HW2FrzStopSet | °C | 4x0264 |  | AV199 |  | 500 | 4000 | 2500 | Water Heating Coil 2: Frost protection Return Water temperature Setpoint during AHU stop [1/100°C]
0x3404 | Heating Coil 2, Water | Set point | Standard | HW2FrzDriftSet | °C | 4x0265 |  | AV200 |  | 200 | 2000 | 500 | Water Heating Coil 2: Frost protection Return Water temperature Setpoint during AHU operation [1/100°C]
0x3405 | Heating Coil 2, Water | Control | Standard | HW2FreezePB | °C | 4x0266 |  | AV201 |  | 200 | 2000 | 500 | Water Heating Coil 2: Frost protection P-band setpoint [1/100°C]
0x3406 | Heating Coil 2, Water | Alarm | Standard | HW2FrzAlrTpSet | °C | 4x0267 |  | AV202 |  | 200 | 2000 | 200 | Water Heating Coil 2: Frost protection Return water temperature alarm setpoint [1/100°C]
0x3352 | Cooling Coil | Set point | Standard | CL_CW_PumpStartPr | % | 4x0268 |  | AV310 |  | 0 | 10000 | 2500 | Water Cooling Coil: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x3923 | Heat Exchanger | Set point | Standard | BattEXCPmpStPr | % | 4x0269 |  | AV309 |  | 0 | 10000 | 2500 | Run Around Coil: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x3358 | Heat Pump | Set point | Special | STMP_HP_MinOpTemp1 | °C | 4x0270 |  | AV215 |  | -4000 | 4000 | 1000 | Heat Pump: DX Compressor 1 Outdoor temperature stop setpoint. Compressor stops at lower temperatures.
0x3359 | Heat Pump | Set point | Special | STMP_HP_MinOpTemp2 | °C | 4x0271 |  | AV216 |  | -4000 | 4000 | 1000 | Heat Pump: DX Compressor 2 Outdoor temperature stop setpoint. Compressor stops at lower temperatures.
0x335A | Heat Pump | Set point | Special | STMP_HP_MinOpTemp3 | °C | 4x0272 |  | AV217 |  | -4000 | 4000 | 1000 | Heat Pump: DX Compressor 3 Outdoor temperature stop setpoint. Compressor stops at lower temperatures.
0x335B | Heat Pump | Set point | Special | STMP_HP_MinOpTemp4 | °C | 4x0273 |  | AV218 |  | -4000 | 4000 | 1000 | Heat Pump: DX Compressor 4 Outdoor temperature stop setpoint. Compressor stops at lower temperatures.
0x3410 | Combi Coil | Set point | Standard | CombiUpStPow | % | 4x0275 |  | AV286 |  | 0 | 10000 | 5000 | Combi Coil: Valve setpoint during AHU start up. [1/100%]
0x3411 | Combi Coil | Control | Standard | CombiPumpFunc |  | 4x0276 |  | AV287 |  | 0 | 3 | 1 | Set Combi Coil Circulator Pump operation mode: 0 = Constant: The Circulator Pump is always On. 1 = Auto: The Circulator Pump starts when active heating is required. 2 = Outdoor Air temp: The Circulator Pump starts at low Outdoor temperatur
0x3412 | Combi Coil | Set point | Standard | STMP_CombiPmpStTmpH | °C | 4x0277 |  | AV288 |  | 500 | 3000 | 1000 | Combi Coil: Outdoor temperature setpoint for start of Circulator Pump. [1/100°C].
0x341C | Combi Coil | Set point | Standard | CombiPmpStPrc | % | 4x0278 |  | AV289 |  | 0 | 10000 | 300 | Combi Coil: Valve setpoint for start of Circulator Pump. [1/100%] The pump starts at higher values.
0x3413 | Combi Coil | Set point |  | STMP_CombFrzStopSet | °C | 4x0279 |  | AV290 |  | 500 | 4000 | 2500 | Combi Coil: Frost protection Return Water temperature Setpoint during AHU stop [1/100°C]
0x3414 | Combi Coil | Set point |  | STMP_CombFrzDrSetH | °C | 4x0280 |  | AV291 |  | 200 | 2000 | 500 | Combi Coil: Frost protection Return Water temperature Setpoint during AHU operation [1/100°C]
0x3415 | Combi Coil | Control | Standard | CombiFrzPB | °C | 4x0281 |  | AV292 |  | 200 | 2000 | 500 | Combi Coil: Frost protection P-band setpoint [1/100°C]
0x3416 | Combi Coil | Set point | Standard | STMP_CombiFrzAlHSet | °C | 4x0282 |  | AV293 |  | 200 | 2000 | 200 | Combi Coil: Frost protection Return water temperature alarm setpoint [1/100°C]
0x3925 | Heat Exchanger | Set point | Standard | BattEXCFrzStop | °C | 4x0283 |  | AV219 |  | -1000 | 4000 | 2500 | Run Around Coil: Frost protection Return Water temperature Setpoint during AHU stop [1/100°C]
0x3926 | Heat Exchanger | Set point | Standard | BattEXCFrzDrf | °C | 4x0284 |  | AV220 |  | -1000 | 2000 | 500 | Run Around Coil: Frost protection Return Water temperature Setpoint during AHU operation [1/100°C]
0x3927 | Heat Exchanger | Control | Standard | BattEXCFrzePB | °C | 4x0285 |  | AV221 |  | 200 | 2000 | 500 | Run Around Coil: Frost protection P-band setpoint [1/100°C]
0x3928 | Heat Exchanger | Set point | Standard | BattEXCFrzASet | °C | 4x0286 |  | AV222 |  | -1000 | 2000 | 200 | Run Around Coil: Frost protection Return water temperature alarm setpoint [1/100°C]
| Combi Coil | Control | Standard | ATMP_CMB_CoilRT | °C | 4x0287 |  | AI126 |  | -5000 | 11000 |  | Current Combi HT-WaterBattTemp [1/100C] Coil/Return
0x33DA | Heating Coil, Water | Control | Special | HW12VDCOutFunc |  | 4x0288 |  | AV225 |  | 0 | 1 | 0 | Special customer code: Heating Coil 1, step 2 output (Out 1,2): Set Valve Actuator type: 0 = 0-10V Valve Actuator. 1 = 2-10V Valve Actuator.
0x34F2 | Heating Coil 2 | Set point | Special | Ht2LimitTyp |  | 4x0290 |  | AV229 |  | 0 | 2 | 0 | Special customer code: Set Heating Coil 2 limiting type: 1 = Room temperature. 2 = Outdoor temperature.
0x34F3 | Heating Coil 2 | Set point | Special | Ht2StLimRTemp | °C | 4x0291 |  | AV230 |  | -500 | 0 | -200 | Special customer code: Set Heating Coil 2 deadband [1/100°C]
0x34F4 | Heating Coil 2 | Set point | Special | Ht2StLimRPer | % | 4x0292 |  | AV231 |  | 1000 | 10000 | 2000 | Special customer code: Set Stepsize for Room temperature limit [1/100%]
0x34F5 | Heating Coil 2 | Set point | Special | Ht2StLimOTemp | °C | 4x0293 |  | AV232 |  | -2000 | 2000 | -500 | Special customer code: Outdoor temperature Setpoint for Block of Heating Coil 2 [1/100°C]
0x34F6 | Heating Coil 2 | Set point | Special | Ht2SetDelTime | Sec | 4x0294 |  | AV234 |  | 0 | 7200 | 3600 | Special customer code: Set Time delay for activation of Heating Coil 2 [Sec]
0x34F7 | Heating Coil 2 | Set point | Special | Ht2FlowOffset | % | 4x0295 |  | AV233 |  | -5000 | 5000 | 5000 | Special customer code: Air Volume increase Setpoint when Heating Coil 2 is on [1/100%]
0x34F1 | Cooling Coil | Set point | Special | NO_CStopRTemp | °C | 4x0296 |  | AV228 |  | 0 | 3000 | 2300 | Special customer code: Room temperature Setpoint for Stop of Active Cooling [1/100°C]
0x3A8E | Cooling Coil | Set point | Special | REXDeIcePerc |  | 4x0297 |  | AV226 |  | 3000 | 10000 | 5000 | Special customer code: Rotary Heat Exchanger Pressure drop De-icing Limit Setpoint (dynamic pressure) [1/100%]
0x34F0 | Cooling Coil | Set point | Special | STMP_NO_FAirCoolBlk | °C | 4x0298 |  | AV227 |  | -4000 | 2000 | 1000 | Special customer code: Outdoor temperature Setpoint for Stop of Freshair Cooling [1/100°C]
0x3488 | Humidity | Set point | Standard | DehumSet_RH |  | 4x0299 |  | AV250 |  | 1000 | 10000 | 7000 | Dehumification Setpoint %rH [1/100%]
0x34F8 | Damper, Recirculation | Control | Special | TR_RecFlowShift |  | 4x0300 |  | AV235 |  | 0 | 2 | 0 | Special customer code: Airflow Setpoint for entering Recirculation mode.
0x34F9 | Damper, Recirculation | Set point | Special | STMP_RecClosDAStart | °C | 4x0301 |  | AV236 |  | -1000 | 2000 | 0 | Special customer code: Outdoor Temperature Setpoint for Ahu start up using open Fresh Air Damper [1/100°C]
0x3A9E | Damper, Recirculation | Alarm | Special | REXAlrLPrcFrz | % | 4x0302 |  | AV308 |  | 0 | 20000 | 12000 | Special customer code: Rotary Heat Exchanger Pressure drop Ice Alarm Limit Setpoint (dynamic pressure) [1/100%]
0x3A9F | Damper, Recirculation | Alarm | Special | REXAlrLPrcDus | % | 4x0303 |  | AV307 |  | 0 | 10000 | 2000 | Special customer code: Rotary Heat Exchanger Pressure drop Dust Alarm Limit Setpoint (dynamic pressure) [1/100%]
0x33DB | Heating Coil, Water | Control | Special | HW1RiseT100 | Sec | 4x0304 |  | AV305 |  | 120 | 7200 | 3600 | Special customer code: Water Heating Coil 1 Risetime from 0..100% Setpoint [Sec]
0x32F5 | Cooling, DX | Set point | Special | ROHRiseT100 | Sec | 4x0305 |  | AV237 |  | 120 | 7200 | 3600 | Special customer code: CO2 DX Cooling Risetime from 0 ..100% Setpoint [Sec]
0x33C8 | AHU Controller | Summer Night Cooling | Standard | SNC_SupCoolFlw | l/s | 4x0306 |  | AV238 |  | 0 | 32000 | 2000 | Summer Night Cooling: Supply Air Volume Setpoint
0x33C9 | AHU Controller | Summer Night Cooling | Standard | SNC_ExtCoolFlw | l/s | 4x0307 |  | AV239 |  | 0 | 32000 | 2000 | Summer Night Cooling: Extract Air Volume Setpoint
0x33CA | AHU Controller | Summer Night Cooling | Standard | SNC_SupCoolPa | Pa | 4x0308 |  | AV240 |  | 0 | 5000 | 50 | Summer Night Cooling: Supply Air Duct Pressure Setpoint
0x33CB | AHU Controller | Summer Night Cooling | Standard | SNC_ExtCoolPa | Pa | 4x0309 |  | AV241 |  | 0 | 5000 | 50 | Summer Night Cooling: Extract Air Duct Pressure Setpoint
0x33CC | AHU Controller | Summer Night Cooling | Standard | SNC_SupCoolPrc | % | 4x0310 |  | AV242 |  | 0 | 10000 | 2000 | Summer Night Cooling: Supply Air Constant Fan speed Setpoint
0x33CD | AHU Controller | Summer Night Cooling | Standard | SNC_ExtCoolPrc | % | 4x0311 |  | AV243 |  | 0 | 10000 | 2000 | Summer Night Cooling: Extract Air Constant Fan speed Setpoint
0x33CE | AHU Controller | Summer Night Cooling | Standard | SNC_SlvOffsPrc | % | 4x0312 |  | AV247 |  | -5000 | 5000 | 0 | Summer Night Cooling: Slave Fan Offset Setpoint [1/100%]
| AHU Controller | Set point | Standard | DewCoolPower | % | 4x0313 |  | AV294 |  | 0 | 10000 |  | Dehumidification: Max. Cooling Power Setpoint [%]. Not active if Dew Point Sensor configured.
0x345B | CO2 Sensor | Set point | Special | AR_CO2_MaxModRec | ppm | 4x0314 |  | AV248 |  | 0 | 10000 | 1000 | Special customer code: Max. CO2 Setpoint (Shop function) [ppm]
0x345C | CO2 Sensor | Set point | Special | AR_CO2_MinModRec | ppm | 4x0315 |  | AV249 |  | 0 | 10000 | 1000 | Special customer code: Min. CO2 Setpoint (Shop function) [ppm]
| AHU controller | Control | Standard | AR_SA_MedSpeedFlowSet | l/s | 4x0320 |  | AV57 |  | 0 | 30000 | 3000 | User SupplyFlow-MediumSpeedSet [l/s]
| AHU controller | Control | Standard | AR_SA_DuctPaMedSet | Pa | 4x0322 |  | AV51 |  | 0 | 5000 | 120 | MediumSpeed DuctPressure Set [Pa]
0x33ED | Damper, Recirculation | Set point | Standard | RecMinFresh | % | 4x0325 |  | AV257 |  | 0 | 10000 | 1000 | Modulated Recirculation: Minimum Fresh Air Setpoint [1/100%]
0x339C | Filter | Alarm | Standard | FiltExt2StaAlr | Pa | 4x0326 |  | AV259 |  | 10 | 500 | 80 | Extract Air Filter 2: Pressure drop Alarm Limit setpoint (static pressure)
0x339D | Filter | Alarm | Standard | FiltSup2DynAlr | % | 4x0327 |  | AV260 |  | 1000 | 10000 | 5000 | Supply Air Filter 2: Pressure drop Alarm Limit Setpoint (dynamic pressure) [1/100%]
0x339E | Filter | Alarm | Standard | FiltExt2DynAlr | % | 4x0328 |  | AV261 |  | 1000 | 10000 | 5000 | Extract Air Filter 2: Pressure drop Alarm Limit setpiont (dynamic pressure) [1/100%]
0x31C0 | Zone 1 | Set point | Standard | ZM1_RoomTmpSet |  | 4x0329 |  | AV262 |  | -4000 | 10000 |  | Zone Module 1 - Room Temperature Setpoint
0x31C1 | Zone 1 | Set point | Standard | ZM1_MinSupTemp |  | 4x0330 |  | AV263 |  | -4000 | 10000 |  | Zone Module 1 - Minimum Supply Temperature Setpoint
0x31C2 | Zone 1 | Set point | Standard | ZM1_MaxSupTemp |  | 4x0331 |  | AV264 |  | -4000 | 10000 |  | Zone Module 1 - Maximum Supply Temperature Setpoint
0x31C3 | Zone 1 | Set point | Standard | ZM1_CO2Set |  | 4x0332 |  | AV265 |  | 0 | 5000 |  | Zone Module 1 - Room CO2 Setpoint
0x31C4 | Zone 1 | Set point | Standard | ZM1_RHSet |  | 4x0333 |  | AV266 |  | 0 | 10000 |  | Zone Module 1 - Room RH Setpoint
0x31C5 | Zone 1 | Set point | Standard | ZM1_PIRMinFlow |  | 4x0334 |  | AV267 |  | 0 | 0 |  | Zone Module 1 - VAV Supply PIR Min Air Flow Setpoint
0x31D0 | Zone 2 | Set point | Standard | ZM2_RoomTmpSet |  | 4x0335 |  | AV268 |  | -4000 | 10000 |  | Zone Module 2 - Room Temperature Setpoint
0x31D1 | Zone 2 | Set point | Standard | ZM2_MinSupTemp |  | 4x0336 |  | AV269 |  | -4000 | 10000 |  | Zone Module 2 - Minimum Supply Temperature Setpoint
0x31D2 | Zone 2 | Set point | Standard | ZM2_MaxSupTemp |  | 4x0337 |  | AV270 |  | -4000 | 10000 |  | Zone Module 2 - Maximum Supply Temperature Setpoint
0x31D3 | Zone 2 | Set point | Standard | ZM2_CO2Set |  | 4x0338 |  | AV271 |  | 0 | 5000 |  | Zone Module 2 - Room CO2 Setpoint
0x31D4 | Zone 2 | Set point | Standard | ZM2_RHSet |  | 4x0339 |  | AV272 |  | 0 | 10000 |  | Zone Module 2 - Room RH Setpoint
0x31D5 | Zone 2 | Set point | Standard | ZM2_PIRMinFlow |  | 4x0340 |  | AV273 |  | 0 | 0 |  | Zone Module 2 - VAV Supply PIR Min Air Flow Setpoint
0x31E0 | Zone 3 | Set point | Standard | ZM3_RoomTmpSet |  | 4x0341 |  | AV274 |  | -4000 | 10000 |  | Zone Module 3 - Room Temperature Setpoint
0x31E1 | Zone 3 | Set point | Standard | ZM3_MinSupTemp |  | 4x0342 |  | AV275 |  | -4000 | 10000 |  | Zone Module 3 - Minimum Supply Temperature Setpoint
0x31E2 | Zone 3 | Set point | Standard | ZM3_MaxSupTemp |  | 4x0343 |  | AV276 |  | -4000 | 10000 |  | Zone Module 3 - Maximum Supply Temperature Setpoint
0x31E3 | Zone 3 | Set point | Standard | ZM3_CO2Set |  | 4x0344 |  | AV277 |  | 0 | 5000 |  | Zone Module 3 - Room CO2 Setpoint
0x31E4 | Zone 3 | Set point | Standard | ZM3_RHSet |  | 4x0345 |  | AV278 |  | 0 | 10000 |  | Zone Module 3 - Room RH Setpoint
0x31E5 | Zone 3 | Set point | Standard | ZM3_PIRMinFlow |  | 4x0346 |  | AV279 |  | 0 | 0 |  | Zone Module 3 - VAV Supply PIR Min Air Flow Setpoint
0x31F0 | Zone 4 | Set point | Standard | ZM4_RoomTmpSet |  | 4x0347 |  | AV280 |  | -4000 | 10000 |  | Zone Module 4 - Room Temperature Setpoint
0x31F1 | Zone 4 | Set point | Standard | ZM4_MinSupTemp |  | 4x0348 |  | AV281 |  | -4000 | 10000 |  | Zone Module 4 - Minimum Supply Temperature Setpoint
0x31F2 | Zone 4 | Set point | Standard | ZM4_MaxSupTemp |  | 4x0349 |  | AV282 |  | -4000 | 10000 |  | Zone Module 4 - Maximum Supply Temperature Setpoint
0x31F3 | Zone 4 | Set point | Standard | ZM4_CO2Set |  | 4x0350 |  | AV283 |  | 0 | 5000 |  | Zone Module 4 - Room CO2 Setpoint
0x31F4 | Zone 4 | Set point | Standard | ZM4_RHSet |  | 4x0351 |  | AV284 |  | 0 | 10000 |  | Zone Module 4 - Room RH Setpoint
0x31F5 | Zone 4 | Set point | Standard | ZM4_PIRMinFlow |  | 4x0352 |  | AV285 |  | 0 | 0 |  | Zone Module 4 - VAV Supply PIR Min Air Flow Setpoint
0x33EF | Damper, Recirculation | Set point | Standard | AR_REC_MaxFreshAir |  | 4x0359 |  | AV304 |  | 3000 | 10000 | 10000 | Modulated Recirculation: Max. Fresh Air Setpoint [1/100%]
0x32FE | AHU Controller | Set point | Special | ROHOutdBlkTmp |  | 4x0360 |  | AV319 |  | -2000 | 5000 | -500 | Special customer code: Outdoor temperature Setpoint for blocking of Heating Coil 2.
| AHU Controller | Set point | Special | TR_TempRegOffset |  | 4x0361 |  | AV322 |  | -200 | 200 | 0 | Temperature Setpoint: Web page Offset Slider Setpoint [1/100C]
| AHU Controller | Set point | Special | DC_Compressor_PercentSet |  | 4x0370 |  | AV323 |  | 0 | 10000 | 0 | Drives Compressor Setpoint/PrcSet
| AHU Controller | Set point | Special | IOC_DI_FP_Oil_HPT_Uset |  | 4x0380 |  | AV324 |  | 0 | 65535 | 0 | IOC Digital input Heatpump Frost / Lubrication
| AHU Controller | Control | Standard | BMSDrfCtrlReg |  | 4x0500 |  | AV108 |  | 0 | 1000 |  | Set AHU operation mode from BMS: 11 = BMS stop 105 = BMS low speed 210 = BMS high speed 211 = BMS summernight cooling 220 = BMS night heating mode (Recirculation) 414 = BMS medium speed BMS-modes are only enabled when digital input "Operating mode via BMS" is active (Input closed)
| Temp. Out door | Current value | Standard | STMP_MBT_OutDoor | °C | 4x0501 |  | AV102 |  | -6000 | 10000 | 0 | BMS Outdoor temperature sensor input [1/100°C]
| Temp. Room | Current value | Standard | STMP_MBT_Room1 | °C | 4x0502 |  | AV103 |  | -4000 | 10000 | 0 | BMS Room temperatur sensor input [1/100°C]
| Scheduler |  |  | Schedule Object Effective Periode |  | Ext. Modbus |  | BacNet Register |  | Min | Max |  | Comments in English
| Scheduler | Object Effective periode |  | SO_EP_StartYear |  | 4x0503 |  |  |  | 2000 | 2099 | 0 | Start Year 2000 2099
| Scheduler | Object Effective periode |  | SO_EP_StartMonth |  | 4x0504 |  |  |  | 0 | 14 | 0 | 0-Unspecified, 13-odd month, 14-even month
| Scheduler | Object Effective periode |  | SO_EP_StartDate |  | 4x0505 |  |  |  | 0 | 34 | 0 | 0-Unspecified, 32-Last day, 33-odd, 34-even day
| Scheduler | Object Effective periode |  | SO_EP_StartWeekday |  | 4x0506 |  |  |  | 0 | 7 | 0 | 0-Unspecified, 1..7 = Monday..Sunday
| Scheduler | Object Effective periode |  | SO_EP_StopYear |  | 4x0507 |  |  |  | 2000 | 2099 | 0 | Stop Year 2000 2099
| Scheduler | Object Effective periode |  | SO_EP_StopMonth |  | 4x0508 |  |  |  | 0 | 14 | 0 | 0-Unspecified, 13-odd month, 14-even month
| Scheduler | Object Effective periode |  | SO_EP_StopDate |  | 4x0509 |  |  |  | 0 | 34 | 0 | 0-Unspecified, 32-Last day, 33-odd, 34-even day
| Scheduler | Object Effective periode |  | SO_EP_StopWeekday |  | 4x0510 |  |  |  | 0 | 7 | 0
| Scheduler | Object Hour Monday |  | SO_WS_MondayHour0 |  | 4x0520 |  |  |  | 0 | 23 |  | Monday Hour Object 0
| Scheduler |  |  | SO_WS_MondayHour1 |  | 4x0521 |  |  |  | 0 | 23 |  | Monday Hour Object 1
| Scheduler |  |  | SO_WS_MondayHour2 |  | 4x0522 |  |  |  | 0 | 23 |  | Monday Hour Object 2
| Scheduler |  |  | SO_WS_MondayHour3 |  | 4x0523 |  |  |  | 0 | 23 |  | Monday Hour Object 3
| Scheduler |  |  | SO_WS_MondayHour4 |  | 4x0524 |  |  |  | 0 | 23 |  | Monday Hour Object 4
| Scheduler |  |  | SO_WS_MondayHour5 |  | 4x0525 |  |  |  | 0 | 23 |  | Monday Hour Object 5
| Scheduler | Object Minute Monday |  | SO_WS_MondayMinute0 |  | 4x0526 |  |  |  | 0 | 59 |  | Monday Minute Object 0
| Scheduler |  |  | SO_WS_MondayMinute1 |  | 4x0527 |  |  |  | 0 | 59 |  | Monday Minute Object 1
| Scheduler |  |  | SO_WS_MondayMinute2 |  | 4x0528 |  |  |  | 0 | 59 |  | Monday Minute Object 2
| Scheduler |  |  | SO_WS_MondayMinute3 |  | 4x0529 |  |  |  | 0 | 59 |  | Monday Minute Object 3
| Scheduler |  |  | SO_WS_MondayMinute4 |  | 4x0530 |  |  |  | 0 | 59 |  | Monday Minute Object 4
| Scheduler |  |  | SO_WS_MondayMinute5 |  | 4x0531 |  |  |  | 0 | 59 |  | Monday Minute Object 5
| Scheduler | Object Value Monday |  | SO_WS_MondayValue0 |  | 4x0532 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_MondayValue1 |  | 4x0533 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_MondayValue2 |  | 4x0534 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_MondayValue3 |  | 4x0535 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_MondayValue4 |  | 4x0536 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_MondayValue5 |  | 4x0537 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Tuesday |  | SO_WS_TuesdayHour0 |  | 4x0538 |  |  |  | 0 | 23 |  | Tuesday Hour Object 0
| Scheduler |  |  | SO_WS_TuesdayHour1 |  | 4x0539 |  |  |  | 0 | 23 |  | Tuesday Hour Object 1
| Scheduler |  |  | SO_WS_TuesdayHour2 |  | 4x0540 |  |  |  | 0 | 23 |  | Tuesday Hour Object 2
| Scheduler |  |  | SO_WS_TuesdayHour3 |  | 4x0541 |  |  |  | 0 | 23 |  | Tuesday Hour Object 3
| Scheduler |  |  | SO_WS_TuesdayHour4 |  | 4x0542 |  |  |  | 0 | 23 |  | Tuesday Hour Object 4
| Scheduler |  |  | SO_WS_TuesdayHour5 |  | 4x0543 |  |  |  | 0 | 23 |  | Tuesday Hour Object 5
| Scheduler | Object Minute Tuesday |  | SO_WS_TuesdayMinute0 |  | 4x0544 |  |  |  | 0 | 59 |  | Tuesday Minute Object 0
| Scheduler |  |  | SO_WS_TuesdayMinute1 |  | 4x0545 |  |  |  | 0 | 59 |  | Tuesday Minute Object 1
| Scheduler |  |  | SO_WS_TuesdayMinute2 |  | 4x0546 |  |  |  | 0 | 59 |  | Tuesday Minute Object 2
| Scheduler |  |  | SO_WS_TuesdayMinute3 |  | 4x0547 |  |  |  | 0 | 59 |  | Tuesday Minute Object 3
| Scheduler |  |  | SO_WS_TuesdayMinute4 |  | 4x0548 |  |  |  | 0 | 59 |  | Tuesday Minute Object 4
| Scheduler |  |  | SO_WS_TuesdayMinute5 |  | 4x0549 |  |  |  | 0 | 59 |  | Tuesday Minute Object 5
| Scheduler | Object Value Tuesday |  | SO_WS_TuesdayValue0 |  | 4x0550 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_TuesdayValue1 |  | 4x0551 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_TuesdayValue2 |  | 4x0552 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_TuesdayValue3 |  | 4x0553 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_TuesdayValue4 |  | 4x0554 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_TuesdayValue5 |  | 4x0555 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Wednesday |  | SO_WS_WednesdayHour0 |  | 4x0556 |  |  |  | 0 | 23 |  | Monday Hour Object 0
| Scheduler |  |  | SO_WS_WednesdayHour1 |  | 4x0557 |  |  |  | 0 | 23 |  | Wednesday Hour Object 1
| Scheduler |  |  | SO_WS_WednesdayHour2 |  | 4x0558 |  |  |  | 0 | 23 |  | Wednesday Hour Object 2
| Scheduler |  |  | SO_WS_WednesdayHour3 |  | 4x0559 |  |  |  | 0 | 23 |  | Wednesday Hour Object 3
| Scheduler |  |  | SO_WS_WednesdayHour4 |  | 4x0560 |  |  |  | 0 | 23 |  | Wednesday Hour Object 4
| Scheduler |  |  | SO_WS_WednesdayHour5 |  | 4x0561 |  |  |  | 0 | 23 |  | Wednesday Hour Object 5
| Scheduler | Object Minute Wednesday |  | SO_WS_WednesdayMinute0 |  | 4x0562 |  |  |  | 0 | 59 |  | Wednesday Minute Object 0
| Scheduler |  |  | SO_WS_WednesdayMinute1 |  | 4x0563 |  |  |  | 0 | 59 |  | Wednesday Minute Object 1
| Scheduler |  |  | SO_WS_WednesdayMinute2 |  | 4x0564 |  |  |  | 0 | 59 |  | Wednesday Minute Object 2
| Scheduler |  |  | SO_WS_WednesdayMinute3 |  | 4x0565 |  |  |  | 0 | 59 |  | Wednesday Minute Object 3
| Scheduler |  |  | SO_WS_WednesdayMinute4 |  | 4x0566 |  |  |  | 0 | 59 |  | Wednesday Minute Object 4
| Scheduler |  |  | SO_WS_WednesdayMinute5 |  | 4x0567 |  |  |  | 0 | 59 |  | Wednesday Minute Object 5
| Scheduler | Object Value Wednesday |  | SO_WS_WednesdayValue0 |  | 4x0568 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_WednesdayValue1 |  | 4x0569 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_WednesdayValue2 |  | 4x0570 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_WednesdayValue3 |  | 4x0571 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_WednesdayValue4 |  | 4x0572 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_WednesdayValue5 |  | 4x0573 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Thursday |  | SO_WS_ThursdayHour0 |  | 4x0574 |  |  |  | 0 | 23 |  | Monday Hour Object 0
| Scheduler |  |  | SO_WS_ThursdayHour1 |  | 4x0575 |  |  |  | 0 | 23 |  | Thursday Hour Object 1
| Scheduler |  |  | SO_WS_ThursdayHour2 |  | 4x0576 |  |  |  | 0 | 23 |  | Thursday Hour Object 2
| Scheduler |  |  | SO_WS_ThursdayHour3 |  | 4x0577 |  |  |  | 0 | 23 |  | Thursday Hour Object 3
| Scheduler |  |  | SO_WS_ThursdayHour4 |  | 4x0578 |  |  |  | 0 | 23 |  | Thursday Hour Object 4
| Scheduler |  |  | SO_WS_ThursdayHour5 |  | 4x0579 |  |  |  | 0 | 23 |  | Thursday Hour Object 5
| Scheduler | Object Minute Thursday |  | SO_WS_ThursdayMinute0 |  | 4x0580 |  |  |  | 0 | 59 |  | Thursday Minute Object 0
| Scheduler |  |  | SO_WS_ThursdayMinute1 |  | 4x0581 |  |  |  | 0 | 59 |  | Thursday Minute Object 1
| Scheduler |  |  | SO_WS_ThursdayMinute2 |  | 4x0582 |  |  |  | 0 | 59 |  | Thursday Minute Object 2
| Scheduler |  |  | SO_WS_ThursdayMinute3 |  | 4x0583 |  |  |  | 0 | 59 |  | Thursday Minute Object 3
| Scheduler |  |  | SO_WS_ThursdayMinute4 |  | 4x0584 |  |  |  | 0 | 59 |  | Thursday Minute Object 4
| Scheduler |  |  | SO_WS_ThursdayMinute5 |  | 4x0585 |  |  |  | 0 | 59 |  | Thursday Minute Object 5
| Scheduler | Object Value Thursday |  | SO_WS_ThursdayValue0 |  | 4x0586 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_ThursdayValue1 |  | 4x0587 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_ThursdayValue2 |  | 4x0588 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_ThursdayValue3 |  | 4x0589 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_ThursdayValue4 |  | 4x0590 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_ThursdayValue5 |  | 4x0591 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Friday |  | SO_WS_FridayHour0 |  | 4x0592 |  |  |  | 0 | 23 |  | Friday Hour Object 0
| Scheduler |  |  | SO_WS_FridayHour1 |  | 4x0593 |  |  |  | 0 | 23 |  | Friday Hour Object 1
| Scheduler |  |  | SO_WS_FridayHour2 |  | 4x0594 |  |  |  | 0 | 23 |  | Friday Hour Object 2
| Scheduler |  |  | SO_WS_FridayHour3 |  | 4x0595 |  |  |  | 0 | 23 |  | Friday Hour Object 3
| Scheduler |  |  | SO_WS_FridayHour4 |  | 4x0596 |  |  |  | 0 | 23 |  | Friday Hour Object 4
| Scheduler |  |  | SO_WS_FridayHour5 |  | 4x0597 |  |  |  | 0 | 23 |  | Friday Hour Object 5
| Scheduler | Object Minute Friday |  | SO_WS_FridayMinute0 |  | 4x0598 |  |  |  | 0 | 59 |  | Friday Minute Object 0
| Scheduler |  |  | SO_WS_FridayMinute1 |  | 4x0599 |  |  |  | 0 | 59 |  | Friday Minute Object 1
| Scheduler |  |  | SO_WS_FridayMinute2 |  | 4x0600 |  |  |  | 0 | 59 |  | Friday Minute Object 2
| Scheduler |  |  | SO_WS_FridayMinute3 |  | 4x0601 |  |  |  | 0 | 59 |  | Friday Minute Object 3
| Scheduler |  |  | SO_WS_FridayMinute4 |  | 4x0602 |  |  |  | 0 | 59 |  | Friday Minute Object 4
| Scheduler |  |  | SO_WS_FridayMinute5 |  | 4x0603 |  |  |  | 0 | 59 |  | Friday Minute Object 5
| Scheduler | Object Value Friday |  | SO_WS_FridayValue0 |  | 4x0604 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_FridayValue1 |  | 4x0605 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_FridayValue2 |  | 4x0606 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_FridayValue3 |  | 4x0607 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_FridayValue4 |  | 4x0608 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_FridayValue5 |  | 4x0609 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Saturday |  | SO_WS_SaturdayHour0 |  | 4x0610 |  |  |  | 0 | 23 |  | Saturday Hour Object 0
| Scheduler |  |  | SO_WS_SaturdayHour1 |  | 4x0611 |  |  |  | 0 | 23 |  | Saturday Hour Object 1
| Scheduler |  |  | SO_WS_SaturdayHour2 |  | 4x0612 |  |  |  | 0 | 23 |  | Saturday Hour Object 2
| Scheduler |  |  | SO_WS_SaturdayHour3 |  | 4x0613 |  |  |  | 0 | 23 |  | Saturday Hour Object 3
| Scheduler |  |  | SO_WS_SaturdayHour4 |  | 4x0614 |  |  |  | 0 | 23 |  | Saturday Hour Object 4
| Scheduler |  |  | SO_WS_SaturdayHour5 |  | 4x0615 |  |  |  | 0 | 23 |  | Saturday Hour Object 5
| Scheduler | Object Minute Saturday |  | SO_WS_SaturdayMinute0 |  | 4x0616 |  |  |  | 0 | 59 |  | Saturday Minute Object 0
| Scheduler |  |  | SO_WS_SaturdayMinute1 |  | 4x0617 |  |  |  | 0 | 59 |  | Saturday Minute Object 1
| Scheduler |  |  | SO_WS_SaturdayMinute2 |  | 4x0618 |  |  |  | 0 | 59 |  | Saturday Minute Object 2
| Scheduler |  |  | SO_WS_SaturdayMinute3 |  | 4x0619 |  |  |  | 0 | 59 |  | Saturday Minute Object 3
| Scheduler |  |  | SO_WS_SaturdayMinute4 |  | 4x0620 |  |  |  | 0 | 59 |  | Saturday Minute Object 4
| Scheduler |  |  | SO_WS_SaturdayMinute5 |  | 4x0621 |  |  |  | 0 | 59 |  | Saturday Minute Object 5
| Scheduler | Object Value Saturday |  | SO_WS_SaturdayValue0 |  | 4x0622 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SaturdayValue1 |  | 4x0623 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SaturdayValue2 |  | 4x0624 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SaturdayValue3 |  | 4x0625 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SaturdayValue4 |  | 4x0626 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SaturdayValue5 |  | 4x0627 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Hour Sunday |  | SO_WS_SundayHour0 |  | 4x0628 |  |  |  | 0 | 23 |  | Sunday Hour Object 0
| Scheduler |  |  | SO_WS_SundayHour1 |  | 4x0629 |  |  |  | 0 | 23 |  | Sunday Hour Object 1
| Scheduler |  |  | SO_WS_SundayHour2 |  | 4x0630 |  |  |  | 0 | 23 |  | Sunday Hour Object 2
| Scheduler |  |  | SO_WS_SundayHour3 |  | 4x0631 |  |  |  | 0 | 23 |  | Sunday Hour Object 3
| Scheduler |  |  | SO_WS_SundayHour4 |  | 4x0632 |  |  |  | 0 | 23 |  | Sunday Hour Object 4
| Scheduler |  |  | SO_WS_SundayHour5 |  | 4x0633 |  |  |  | 0 | 23 |  | Sunday Hour Object 5
| Scheduler | Object Minute Sunday |  | SO_WS_SundayMinute0 |  | 4x0634 |  |  |  | 0 | 59 |  | Sunday Minute Object 0
| Scheduler |  |  | SO_WS_SundayMinute1 |  | 4x0635 |  |  |  | 0 | 59 |  | Sunday Minute Object 1
| Scheduler |  |  | SO_WS_SundayMinute2 |  | 4x0636 |  |  |  | 0 | 59 |  | Sunday Minute Object 2
| Scheduler |  |  | SO_WS_SundayMinute3 |  | 4x0637 |  |  |  | 0 | 59 |  | Sunday Minute Object 3
| Scheduler |  |  | SO_WS_SundayMinute4 |  | 4x0638 |  |  |  | 0 | 59 |  | Sunday Minute Object 4
| Scheduler |  |  | SO_WS_SundayMinute5 |  | 4x0639 |  |  |  | 0 | 59 |  | Sunday Minute Object 5
| Scheduler | Object Value Sunday |  | SO_WS_SundayValue0 |  | 4x0640 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SundayValue1 |  | 4x0641 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SundayValue2 |  | 4x0642 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SundayValue3 |  | 4x0643 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SundayValue4 |  | 4x0644 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_WS_SundayValue5 |  | 4x0645 |  |  |  | 0 | 5 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Exception - 1 |  | SO_ES_1_StartYear |  | 4x0646 |  |  |  | 2000 | 2099 |  | Exception 1 StartYear
| Scheduler |  |  | SO_ES_1_StartMonth |  | 4x0647 |  |  |  | 0 | 14 |  | Exception 1 StartMonth
| Scheduler |  |  | SO_ES_1_StartDate |  | 4x0648 |  |  |  | 0 | 34 |  | Exception 1 StartDate
| Scheduler |  |  | SO_ES_1_StartWeekday |  | 4x0649 |  |  |  | 0 | 7 |  | Exception 1 StartWeekday
| Scheduler |  |  | SO_ES_1_StopYear |  | 4x0650 |  |  |  | 2000 | 2099 |  | Exception 1 StopYear
| Scheduler |  |  | SO_ES_1_StopMonth |  | 4x0651 |  |  |  | 0 | 14 |  | Exception 1 StopMonth
| Scheduler |  |  | SO_ES_1_StopDate |  | 4x0652 |  |  |  | 0 | 34 |  | Exception 1 StopDate
| Scheduler |  |  | SO_ES_1_StopWeekday |  | 4x0653 |  |  |  | 0 | 7 |  | Exception 1 StopWeekday
| Scheduler |  |  | SO_ES_1_Period |  | 4x0654 |  |  |  | 0 | 5 |  | Exception 1 Period
| Scheduler |  |  | SO_ES_1_EventPriority |  | 4x0655 |  |  |  | 1 | 16 |  | Exception 1 EventPriority
| Scheduler |  |  | SO_ES_1_Hour0 |  | 4x0656 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Hour1 |  | 4x0657 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Hour2 |  | 4x0658 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Hour3 |  | 4x0659 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Hour4 |  | 4x0660 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Hour5 |  | 4x0661 |  |  |  | 0 | 23 |  | Exception 1 Hour 0..6
| Scheduler |  |  | SO_ES_1_Minute0 |  | 4x0662 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Minute1 |  | 4x0663 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Minute2 |  | 4x0664 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Minute3 |  | 4x0665 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Minute4 |  | 4x0666 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Minute5 |  | 4x0667 |  |  |  | 0 | 59 |  | Exception 1 Minute 0..6
| Scheduler |  |  | SO_ES_1_Value0 |  | 4x0668 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_1_Value1 |  | 4x0669 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_1_Value2 |  | 4x0670 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_1_Value3 |  | 4x0671 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_1_Value4 |  | 4x0672 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_1_Value5 |  | 4x0673 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Exception - 2 |  | SO_ES_2_StartYear |  | 4x0674 |  |  |  | 2000 | 2099 |  | Exception 2 StartYear
| Scheduler |  |  | SO_ES_2_StartMonth |  | 4x0675 |  |  |  | 0 | 14 |  | Exception 2 StartMonth
| Scheduler |  |  | SO_ES_2_StartDate |  | 4x0676 |  |  |  | 0 | 34 |  | Exception 2 StartDate
| Scheduler |  |  | SO_ES_2_StartWeekday |  | 4x0677 |  |  |  | 0 | 7 |  | Exception 2 StartWeekday
| Scheduler |  |  | SO_ES_2_StopYear |  | 4x0678 |  |  |  | 2000 | 2099 |  | Exception 2 StopYear
| Scheduler |  |  | SO_ES_2_StopMonth |  | 4x0679 |  |  |  | 0 | 14 |  | Exception 2 StopMonth
| Scheduler |  |  | SO_ES_2_StopDate |  | 4x0680 |  |  |  | 0 | 34 |  | Exception 2 StopDate
| Scheduler |  |  | SO_ES_2_StopWeekday |  | 4x0681 |  |  |  | 0 | 7 |  | Exception 2 StopWeekday
| Scheduler |  |  | SO_ES_2_Period |  | 4x0682 |  |  |  | 0 | 5 |  | Exception 2 Period
| Scheduler |  |  | SO_ES_2_EventPriority |  | 4x0683 |  |  |  | 1 | 16 |  | Exception 2 EventPriority
| Scheduler |  |  | SO_ES_2_Hour0 |  | 4x0684 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Hour1 |  | 4x0685 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Hour2 |  | 4x0686 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Hour3 |  | 4x0687 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Hour4 |  | 4x0688 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Hour5 |  | 4x0689 |  |  |  | 0 | 23 |  | Exception 2 Hour 0..6
| Scheduler |  |  | SO_ES_2_Minute0 |  | 4x0690 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Minute1 |  | 4x0691 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Minute2 |  | 4x0692 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Minute3 |  | 4x0693 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Minute4 |  | 4x0694 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Minute5 |  | 4x0695 |  |  |  | 0 | 59 |  | Exception 2 Minute 0..6
| Scheduler |  |  | SO_ES_2_Value0 |  | 4x0696 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_2_Value1 |  | 4x0697 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_2_Value2 |  | 4x0698 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_2_Value3 |  | 4x0699 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_2_Value4 |  | 4x0700 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_2_Value5 |  | 4x0701 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Object Exception - 3 |  | SO_ES_3_StartYear |  | 4x0702 |  |  |  | 2000 | 2099 |  | Exception 3 StartYear
| Scheduler |  |  | SO_ES_3_StartMonth |  | 4x0703 |  |  |  | 0 | 14 |  | Exception 3 StartMonth
| Scheduler |  |  | SO_ES_3_StartDate |  | 4x0704 |  |  |  | 0 | 34 |  | Exception 3 StartDate
| Scheduler |  |  | SO_ES_3_StartWeekday |  | 4x0705 |  |  |  | 0 | 7 |  | Exception 3 StartWeekday
| Scheduler |  |  | SO_ES_3_StopYear |  | 4x0706 |  |  |  | 2000 | 2099 |  | Exception 3 StopYear
| Scheduler |  |  | SO_ES_3_StopMonth |  | 4x0707 |  |  |  | 0 | 14 |  | Exception 3 StopMonth
| Scheduler |  |  | SO_ES_3_StopDate |  | 4x0708 |  |  |  | 0 | 34 |  | Exception 3 StopDate
| Scheduler |  |  | SO_ES_3_StopWeekday |  | 4x0709 |  |  |  | 0 | 7 |  | Exception 3 StopWeekday
| Scheduler |  |  | SO_ES_3_Period |  | 4x0710 |  |  |  | 0 | 5 |  | Exception 3 Period
| Scheduler |  |  | SO_ES_3_EventPriority |  | 4x0711 |  |  |  | 1 | 16 |  | Exception 3 EventPriority
| Scheduler |  |  | SO_ES_3_Hour0 |  | 4x0712 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Hour1 |  | 4x0713 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Hour2 |  | 4x0714 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Hour3 |  | 4x0715 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Hour4 |  | 4x0716 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Hour5 |  | 4x0717 |  |  |  | 0 | 23 |  | Exception 3 Hour 0..6
| Scheduler |  |  | SO_ES_3_Minute0 |  | 4x0718 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Minute1 |  | 4x0719 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Minute2 |  | 4x0720 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Minute3 |  | 4x0721 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Minute4 |  | 4x0722 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Minute5 |  | 4x0723 |  |  |  | 0 | 59 |  | Exception 3 Minute 0..6
| Scheduler |  |  | SO_ES_3_Value0 |  | 4x0724 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_3_Value1 |  | 4x0725 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_3_Value2 |  | 4x0726 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_3_Value3 |  | 4x0727 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_3_Value4 |  | 4x0728 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler |  |  | SO_ES_3_Value5 |  | 4x0729 |  |  |  | 0 | 6 |  | 0/6-OFF, 1-Stop1, 2-Low, 3-Med, 4-High, 5-Stop2
| Scheduler | Calendar Object 1 |  | CO_DL_1_StartYear0 |  | 4x0730 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_0
| Scheduler |  |  | CO_DL_1_StartYear1 |  | 4x0731 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_1
| Scheduler |  |  | CO_DL_1_StartYear2 |  | 4x0732 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_2
| Scheduler |  |  | CO_DL_1_StartYear3 |  | 4x0733 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_3
| Scheduler |  |  | CO_DL_1_StartYear4 |  | 4x0734 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_4
| Scheduler |  |  | CO_DL_1_StartYear5 |  | 4x0735 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_5
| Scheduler |  |  | CO_DL_1_StartYear6 |  | 4x0736 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_6
| Scheduler |  |  | CO_DL_1_StartYear7 |  | 4x0737 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_7
| Scheduler |  |  | CO_DL_1_StartYear8 |  | 4x0738 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_8
| Scheduler |  |  | CO_DL_1_StartYear9 |  | 4x0739 |  |  |  | 2000 | 2099 |  | Calendar Object 1 Start Year_9
| Scheduler |  |  | CO_DL_1_StartMonth0 |  | 4x0740 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_0
| Scheduler |  |  | CO_DL_1_StartMonth1 |  | 4x0741 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_1
| Scheduler |  |  | CO_DL_1_StartMonth2 |  | 4x0742 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_2
| Scheduler |  |  | CO_DL_1_StartMonth3 |  | 4x0743 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_3
| Scheduler |  |  | CO_DL_1_StartMonth4 |  | 4x0744 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_4
| Scheduler |  |  | CO_DL_1_StartMonth5 |  | 4x0745 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_5
| Scheduler |  |  | CO_DL_1_StartMonth6 |  | 4x0746 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_6
| Scheduler |  |  | CO_DL_1_StartMonth7 |  | 4x0747 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_7
| Scheduler |  |  | CO_DL_1_StartMonth8 |  | 4x0748 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_8
| Scheduler |  |  | CO_DL_1_StartMonth9 |  | 4x0749 |  |  |  | 0 | 14 |  | Calendar Object 1 Start Month_9
| Scheduler |  |  | CO_DL_1_StartDate0 |  | 4x0750 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_0
| Scheduler |  |  | CO_DL_1_StartDate1 |  | 4x0751 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_1
| Scheduler |  |  | CO_DL_1_StartDate2 |  | 4x0752 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_2
| Scheduler |  |  | CO_DL_1_StartDate3 |  | 4x0753 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_3
| Scheduler |  |  | CO_DL_1_StartDate4 |  | 4x0754 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_4
| Scheduler |  |  | CO_DL_1_StartDate5 |  | 4x0755 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_5
| Scheduler |  |  | CO_DL_1_StartDate6 |  | 4x0756 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_6
| Scheduler |  |  | CO_DL_1_StartDate7 |  | 4x0757 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_7
| Scheduler |  |  | CO_DL_1_StartDate8 |  | 4x0758 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_8
| Scheduler |  |  | CO_DL_1_StartDate9 |  | 4x0759 |  |  |  | 0 | 34 |  | Calendar Object 1 Start Date_9
| Scheduler |  |  | CO_DL_1_StartWeekday0 |  | 4x0760 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_0
| Scheduler |  |  | CO_DL_1_StartWeekday1 |  | 4x0761 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_1
| Scheduler |  |  | CO_DL_1_StartWeekday2 |  | 4x0762 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_2
| Scheduler |  |  | CO_DL_1_StartWeekday3 |  | 4x0763 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_3
| Scheduler |  |  | CO_DL_1_StartWeekday4 |  | 4x0764 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_4
| Scheduler |  |  | CO_DL_1_StartWeekday5 |  | 4x0765 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_5
| Scheduler |  |  | CO_DL_1_StartWeekday6 |  | 4x0766 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_6
| Scheduler |  |  | CO_DL_1_StartWeekday7 |  | 4x0767 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_7
| Scheduler |  |  | CO_DL_1_StartWeekday8 |  | 4x0768 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_8
| Scheduler |  |  | CO_DL_1_StartWeekday9 |  | 4x0769 |  |  |  | 0 | 7 |  | Calendar Object 1 Start Weekday_9
| Scheduler |  |  | CO_DL_1_StopYear0 |  | 4x0770 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_0
| Scheduler |  |  | CO_DL_1_StopYear1 |  | 4x0771 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_1
| Scheduler |  |  | CO_DL_1_StopYear2 |  | 4x0772 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_2
| Scheduler |  |  | CO_DL_1_StopYear3 |  | 4x0773 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_3
| Scheduler |  |  | CO_DL_1_StopYear4 |  | 4x0774 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_4
| Scheduler |  |  | CO_DL_1_StopYear5 |  | 4x0775 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_5
| Scheduler |  |  | CO_DL_1_StopYear6 |  | 4x0776 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_6
| Scheduler |  |  | CO_DL_1_StopYear7 |  | 4x0777 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_7
| Scheduler |  |  | CO_DL_1_StopYear8 |  | 4x0778 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_8
| Scheduler |  |  | CO_DL_1_StopYear9 |  | 4x0779 |  |  |  | 2000 | 2099 |  | Calendar_ Object 1 Stop Year_9
| Scheduler |  |  | CO_DL_1_StopMonth0 |  | 4x0780 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_0
| Scheduler |  |  | CO_DL_1_StopMonth1 |  | 4x0781 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_1
| Scheduler |  |  | CO_DL_1_StopMonth2 |  | 4x0782 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_2
| Scheduler |  |  | CO_DL_1_StopMonth3 |  | 4x0783 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_3
| Scheduler |  |  | CO_DL_1_StopMonth4 |  | 4x0784 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_4
| Scheduler |  |  | CO_DL_1_StopMonth5 |  | 4x0785 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_5
| Scheduler |  |  | CO_DL_1_StopMonth6 |  | 4x0786 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_6
| Scheduler |  |  | CO_DL_1_StopMonth7 |  | 4x0787 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_7
| Scheduler |  |  | CO_DL_1_StopMonth8 |  | 4x0788 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_8
| Scheduler |  |  | CO_DL_1_StopMonth9 |  | 4x0789 |  |  |  | 0 | 14 |  | Calendar Object 1 Stop Month_9
| Scheduler |  |  | CO_DL_1_StopDate0 |  | 4x0790 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_0
| Scheduler |  |  | CO_DL_1_StopDate1 |  | 4x0791 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_1
| Scheduler |  |  | CO_DL_1_StopDate2 |  | 4x0792 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_2
| Scheduler |  |  | CO_DL_1_StopDate3 |  | 4x0793 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_3
| Scheduler |  |  | CO_DL_1_StopDate4 |  | 4x0794 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_4
| Scheduler |  |  | CO_DL_1_StopDate5 |  | 4x0795 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_5
| Scheduler |  |  | CO_DL_1_StopDate6 |  | 4x0796 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_6
| Scheduler |  |  | CO_DL_1_StopDate7 |  | 4x0797 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_7
| Scheduler |  |  | CO_DL_1_StopDate8 |  | 4x0798 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_8
| Scheduler |  |  | CO_DL_1_StopDate9 |  | 4x0799 |  |  |  | 0 | 34 |  | Calendar Object 1 Stop Date_9
| Scheduler |  |  | CO_DL_1_StopWeekday0 |  | 4x0800 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_0
| Scheduler |  |  | CO_DL_1_StopWeekday1 |  | 4x0801 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_1
| Scheduler |  |  | CO_DL_1_StopWeekday2 |  | 4x0802 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_2
| Scheduler |  |  | CO_DL_1_StopWeekday3 |  | 4x0803 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_3
| Scheduler |  |  | CO_DL_1_StopWeekday4 |  | 4x0804 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_4
| Scheduler |  |  | CO_DL_1_StopWeekday5 |  | 4x0805 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_5
| Scheduler |  |  | CO_DL_1_StopWeekday6 |  | 4x0806 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_6
| Scheduler |  |  | CO_DL_1_StopWeekday7 |  | 4x0807 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_7
| Scheduler |  |  | CO_DL_1_StopWeekday8 |  | 4x0808 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_8
| Scheduler |  |  | CO_DL_1_StopWeekday9 |  | 4x0809 |  |  |  | 0 | 7 |  | Calendar Object 1 Stop Weekday_9
| Scheduler |  |  | CO_DL_1_Period0 |  | 4x0810 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_0
| Scheduler |  |  | CO_DL_1_Period1 |  | 4x0811 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_1
| Scheduler |  |  | CO_DL_1_Period2 |  | 4x0812 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_2
| Scheduler |  |  | CO_DL_1_Period3 |  | 4x0813 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_3
| Scheduler |  |  | CO_DL_1_Period4 |  | 4x0814 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_4
| Scheduler |  |  | CO_DL_1_Period5 |  | 4x0815 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_5
| Scheduler |  |  | CO_DL_1_Period6 |  | 4x0816 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_6
| Scheduler |  |  | CO_DL_1_Period7 |  | 4x0817 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_7
| Scheduler |  |  | CO_DL_1_Period8 |  | 4x0818 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_8
| Scheduler |  |  | CO_DL_1_Period9 |  | 4x0819 |  |  |  | 0 | 3 |  | Calendar Object 1 Stop Period_9
| Scheduler | Calendar Object 2 |  | CO_DL_2_StartYear0 |  | 4x0820 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_0
| Scheduler |  |  | CO_DL_2_StartYear1 |  | 4x0821 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_1
| Scheduler |  |  | CO_DL_2_StartYear2 |  | 4x0822 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_2
| Scheduler |  |  | CO_DL_2_StartYear3 |  | 4x0823 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_3
| Scheduler |  |  | CO_DL_2_StartYear4 |  | 4x0824 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_4
| Scheduler |  |  | CO_DL_2_StartYear5 |  | 4x0825 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_5
| Scheduler |  |  | CO_DL_2_StartYear6 |  | 4x0826 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_6
| Scheduler |  |  | CO_DL_2_StartYear7 |  | 4x0827 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_7
| Scheduler |  |  | CO_DL_2_StartYear8 |  | 4x0828 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_8
| Scheduler |  |  | CO_DL_2_StartYear9 |  | 4x0829 |  |  |  | 2000 | 2099 |  | Calendar Object 2 Start Year_9
| Scheduler |  |  | CO_DL_2_StartMonth0 |  | 4x0830 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_0
| Scheduler |  |  | CO_DL_2_StartMonth1 |  | 4x0831 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_1
| Scheduler |  |  | CO_DL_2_StartMonth2 |  | 4x0832 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_2
| Scheduler |  |  | CO_DL_2_StartMonth3 |  | 4x0833 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_3
| Scheduler |  |  | CO_DL_2_StartMonth4 |  | 4x0834 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_4
| Scheduler |  |  | CO_DL_2_StartMonth5 |  | 4x0835 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_5
| Scheduler |  |  | CO_DL_2_StartMonth6 |  | 4x0836 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_6
| Scheduler |  |  | CO_DL_2_StartMonth7 |  | 4x0837 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_7
| Scheduler |  |  | CO_DL_2_StartMonth8 |  | 4x0838 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_8
| Scheduler |  |  | CO_DL_2_StartMonth9 |  | 4x0839 |  |  |  | 0 | 14 |  | Calendar Object 2 Start Month_9
| Scheduler |  |  | CO_DL_2_StartDate0 |  | 4x0840 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_0
| Scheduler |  |  | CO_DL_2_StartDate1 |  | 4x0841 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_1
| Scheduler |  |  | CO_DL_2_StartDate2 |  | 4x0842 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_2
| Scheduler |  |  | CO_DL_2_StartDate3 |  | 4x0843 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_3
| Scheduler |  |  | CO_DL_2_StartDate4 |  | 4x0844 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_4
| Scheduler |  |  | CO_DL_2_StartDate5 |  | 4x0845 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_5
| Scheduler |  |  | CO_DL_2_StartDate6 |  | 4x0846 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_6
| Scheduler |  |  | CO_DL_2_StartDate7 |  | 4x0847 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_7
| Scheduler |  |  | CO_DL_2_StartDate8 |  | 4x0848 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_8
| Scheduler |  |  | CO_DL_2_StartDate9 |  | 4x0849 |  |  |  | 0 | 34 |  | Calendar Object 2 Start Date_9
| Scheduler |  |  | CO_DL_2_StartWeekday0 |  | 4x0850 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_0
| Scheduler |  |  | CO_DL_2_StartWeekday1 |  | 4x0851 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_1
| Scheduler |  |  | CO_DL_2_StartWeekday2 |  | 4x0852 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_2
| Scheduler |  |  | CO_DL_2_StartWeekday3 |  | 4x0853 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_3
| Scheduler |  |  | CO_DL_2_StartWeekday4 |  | 4x0854 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_4
| Scheduler |  |  | CO_DL_2_StartWeekday5 |  | 4x0855 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_5
| Scheduler |  |  | CO_DL_2_StartWeekday6 |  | 4x0856 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_6
| Scheduler |  |  | CO_DL_2_StartWeekday7 |  | 4x0857 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_7
| Scheduler |  |  | CO_DL_2_StartWeekday8 |  | 4x0858 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_8
| Scheduler |  |  | CO_DL_2_StartWeekday9 |  | 4x0859 |  |  |  | 0 | 7 |  | Calendar Object 2 Start Weekday_9
| Scheduler |  |  | CO_DL_2_StopYear0 |  | 4x0860 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_0
| Scheduler |  |  | CO_DL_2_StopYear1 |  | 4x0861 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_1
| Scheduler |  |  | CO_DL_2_StopYear2 |  | 4x0862 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_2
| Scheduler |  |  | CO_DL_2_StopYear3 |  | 4x0863 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_3
| Scheduler |  |  | CO_DL_2_StopYear4 |  | 4x0864 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_4
| Scheduler |  |  | CO_DL_2_StopYear5 |  | 4x0865 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_5
| Scheduler |  |  | CO_DL_2_StopYear6 |  | 4x0866 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_6
| Scheduler |  |  | CO_DL_2_StopYear7 |  | 4x0867 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_7
| Scheduler |  |  | CO_DL_2_StopYear8 |  | 4x0868 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_8
| Scheduler |  |  | CO_DL_2_StopYear9 |  | 4x0869 |  |  |  | 2000 | 2099 |  | Calendar_ Object 2 Stop Year_9
| Scheduler |  |  | CO_DL_2_StopMonth0 |  | 4x0870 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_0
| Scheduler |  |  | CO_DL_2_StopMonth1 |  | 4x0871 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_1
| Scheduler |  |  | CO_DL_2_StopMonth2 |  | 4x0872 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_2
| Scheduler |  |  | CO_DL_2_StopMonth3 |  | 4x0873 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_3
| Scheduler |  |  | CO_DL_2_StopMonth4 |  | 4x0874 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_4
| Scheduler |  |  | CO_DL_2_StopMonth5 |  | 4x0875 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_5
| Scheduler |  |  | CO_DL_2_StopMonth6 |  | 4x0876 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_6
| Scheduler |  |  | CO_DL_2_StopMonth7 |  | 4x0877 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_7
| Scheduler |  |  | CO_DL_2_StopMonth8 |  | 4x0878 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_8
| Scheduler |  |  | CO_DL_2_StopMonth9 |  | 4x0879 |  |  |  | 0 | 14 |  | Calendar Object 2 Stop Month_9
| Scheduler |  |  | CO_DL_2_StopDate0 |  | 4x0880 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_0
| Scheduler |  |  | CO_DL_2_StopDate1 |  | 4x0881 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_1
| Scheduler |  |  | CO_DL_2_StopDate2 |  | 4x0882 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_2
| Scheduler |  |  | CO_DL_2_StopDate3 |  | 4x0883 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_3
| Scheduler |  |  | CO_DL_2_StopDate4 |  | 4x0884 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_4
| Scheduler |  |  | CO_DL_2_StopDate5 |  | 4x0885 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_5
| Scheduler |  |  | CO_DL_2_StopDate6 |  | 4x0886 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_6
| Scheduler |  |  | CO_DL_2_StopDate7 |  | 4x0887 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_7
| Scheduler |  |  | CO_DL_2_StopDate8 |  | 4x0888 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_8
| Scheduler |  |  | CO_DL_2_StopDate9 |  | 4x0889 |  |  |  | 0 | 34 |  | Calendar Object 2 Stop Date_9
| Scheduler |  |  | CO_DL_2_StopWeekday0 |  | 4x0890 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_0
| Scheduler |  |  | CO_DL_2_StopWeekday1 |  | 4x0891 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_1
| Scheduler |  |  | CO_DL_2_StopWeekday2 |  | 4x0892 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_2
| Scheduler |  |  | CO_DL_2_StopWeekday3 |  | 4x0893 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_3
| Scheduler |  |  | CO_DL_2_StopWeekday4 |  | 4x0894 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_4
| Scheduler |  |  | CO_DL_2_StopWeekday5 |  | 4x0895 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_5
| Scheduler |  |  | CO_DL_2_StopWeekday6 |  | 4x0896 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_6
| Scheduler |  |  | CO_DL_2_StopWeekday7 |  | 4x0897 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_7
| Scheduler |  |  | CO_DL_2_StopWeekday8 |  | 4x0898 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_8
| Scheduler |  |  | CO_DL_2_StopWeekday9 |  | 4x0899 |  |  |  | 0 | 7 |  | Calendar Object 2 Stop Weekday_9
| Scheduler |  |  | CO_DL_2_Period0 |  | 4x0900 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_0
| Scheduler |  |  | CO_DL_2_Period1 |  | 4x0901 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_1
| Scheduler |  |  | CO_DL_2_Period2 |  | 4x0902 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_2
| Scheduler |  |  | CO_DL_2_Period3 |  | 4x0903 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_3
| Scheduler |  |  | CO_DL_2_Period4 |  | 4x0904 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_4
| Scheduler |  |  | CO_DL_2_Period5 |  | 4x0905 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_5
| Scheduler |  |  | CO_DL_2_Period6 |  | 4x0906 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_6
| Scheduler |  |  | CO_DL_2_Period7 |  | 4x0907 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_7
| Scheduler |  |  | CO_DL_2_Period8 |  | 4x0908 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_8
| Scheduler |  |  | CO_DL_2_Period9 |  | 4x0909 |  |  |  | 0 | 3 |  | Calendar Object 2 Stop Period_9
| Scheduler | Calendar Object 3 |  | CO_DL_3_StartYear0 |  | 4x0910 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_0
| Scheduler |  |  | CO_DL_3_StartYear1 |  | 4x0911 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_1
| Scheduler |  |  | CO_DL_3_StartYear2 |  | 4x0912 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_2
| Scheduler |  |  | CO_DL_3_StartYear3 |  | 4x0913 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_3
| Scheduler |  |  | CO_DL_3_StartYear4 |  | 4x0914 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_4
| Scheduler |  |  | CO_DL_3_StartYear5 |  | 4x0915 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_5
| Scheduler |  |  | CO_DL_3_StartYear6 |  | 4x0916 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_6
| Scheduler |  |  | CO_DL_3_StartYear7 |  | 4x0917 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_7
| Scheduler |  |  | CO_DL_3_StartYear8 |  | 4x0918 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_8
| Scheduler |  |  | CO_DL_3_StartYear9 |  | 4x0919 |  |  |  | 2000 | 2099 |  | Calendar Object 3 Start Year_9
| Scheduler |  |  | CO_DL_3_StartMonth0 |  | 4x0920 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_0
| Scheduler |  |  | CO_DL_3_StartMonth1 |  | 4x0921 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_1
| Scheduler |  |  | CO_DL_3_StartMonth2 |  | 4x0922 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_2
| Scheduler |  |  | CO_DL_3_StartMonth3 |  | 4x0923 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_3
| Scheduler |  |  | CO_DL_3_StartMonth4 |  | 4x0924 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_4
| Scheduler |  |  | CO_DL_3_StartMonth5 |  | 4x0925 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_5
| Scheduler |  |  | CO_DL_3_StartMonth6 |  | 4x0926 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_6
| Scheduler |  |  | CO_DL_3_StartMonth7 |  | 4x0927 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_7
| Scheduler |  |  | CO_DL_3_StartMonth8 |  | 4x0928 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_8
| Scheduler |  |  | CO_DL_3_StartMonth9 |  | 4x0929 |  |  |  | 0 | 14 |  | Calendar Object 3 Start Month_9
| Scheduler |  |  | CO_DL_3_StartDate0 |  | 4x0930 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_0
| Scheduler |  |  | CO_DL_3_StartDate1 |  | 4x0931 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_1
| Scheduler |  |  | CO_DL_3_StartDate2 |  | 4x0932 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_2
| Scheduler |  |  | CO_DL_3_StartDate3 |  | 4x0933 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_3
| Scheduler |  |  | CO_DL_3_StartDate4 |  | 4x0934 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_4
| Scheduler |  |  | CO_DL_3_StartDate5 |  | 4x0935 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_5
| Scheduler |  |  | CO_DL_3_StartDate6 |  | 4x0936 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_6
| Scheduler |  |  | CO_DL_3_StartDate7 |  | 4x0937 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_7
| Scheduler |  |  | CO_DL_3_StartDate8 |  | 4x0938 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_8
| Scheduler |  |  | CO_DL_3_StartDate9 |  | 4x0939 |  |  |  | 0 | 34 |  | Calendar Object 3 Start Date_9
| Scheduler |  |  | CO_DL_3_StartWeekday0 |  | 4x0940 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_0
| Scheduler |  |  | CO_DL_3_StartWeekday1 |  | 4x0941 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_1
| Scheduler |  |  | CO_DL_3_StartWeekday2 |  | 4x0942 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_2
| Scheduler |  |  | CO_DL_3_StartWeekday3 |  | 4x0943 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_3
| Scheduler |  |  | CO_DL_3_StartWeekday4 |  | 4x0944 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_4
| Scheduler |  |  | CO_DL_3_StartWeekday5 |  | 4x0945 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_5
| Scheduler |  |  | CO_DL_3_StartWeekday6 |  | 4x0946 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_6
| Scheduler |  |  | CO_DL_3_StartWeekday7 |  | 4x0947 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_7
| Scheduler |  |  | CO_DL_3_StartWeekday8 |  | 4x0948 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_8
| Scheduler |  |  | CO_DL_3_StartWeekday9 |  | 4x0949 |  |  |  | 0 | 7 |  | Calendar Object 3 Start Weekday_9
| Scheduler |  |  | CO_DL_3_StopYear0 |  | 4x0950 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_0
| Scheduler |  |  | CO_DL_3_StopYear1 |  | 4x0951 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_1
| Scheduler |  |  | CO_DL_3_StopYear2 |  | 4x0952 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_2
| Scheduler |  |  | CO_DL_3_StopYear3 |  | 4x0953 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_3
| Scheduler |  |  | CO_DL_3_StopYear4 |  | 4x0954 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_4
| Scheduler |  |  | CO_DL_3_StopYear5 |  | 4x0955 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_5
| Scheduler |  |  | CO_DL_3_StopYear6 |  | 4x0956 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_6
| Scheduler |  |  | CO_DL_3_StopYear7 |  | 4x0957 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_7
| Scheduler |  |  | CO_DL_3_StopYear8 |  | 4x0958 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_8
| Scheduler |  |  | CO_DL_3_StopYear9 |  | 4x0959 |  |  |  | 2000 | 2099 |  | Calendar_ Object 3 Stop Year_9
| Scheduler |  |  | CO_DL_3_StopMonth0 |  | 4x0960 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_0
| Scheduler |  |  | CO_DL_3_StopMonth1 |  | 4x0961 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_1
| Scheduler |  |  | CO_DL_3_StopMonth2 |  | 4x0962 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_2
| Scheduler |  |  | CO_DL_3_StopMonth3 |  | 4x0963 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_3
| Scheduler |  |  | CO_DL_3_StopMonth4 |  | 4x0964 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_4
| Scheduler |  |  | CO_DL_3_StopMonth5 |  | 4x0965 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_5
| Scheduler |  |  | CO_DL_3_StopMonth6 |  | 4x0966 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_6
| Scheduler |  |  | CO_DL_3_StopMonth7 |  | 4x0967 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_7
| Scheduler |  |  | CO_DL_3_StopMonth8 |  | 4x0968 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_8
| Scheduler |  |  | CO_DL_3_StopMonth9 |  | 4x0969 |  |  |  | 0 | 14 |  | Calendar Object 3 Stop Month_9
| Scheduler |  |  | CO_DL_3_StopDate0 |  | 4x0970 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_0
| Scheduler |  |  | CO_DL_3_StopDate1 |  | 4x0971 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_1
| Scheduler |  |  | CO_DL_3_StopDate2 |  | 4x0972 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_2
| Scheduler |  |  | CO_DL_3_StopDate3 |  | 4x0973 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_3
| Scheduler |  |  | CO_DL_3_StopDate4 |  | 4x0974 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_4
| Scheduler |  |  | CO_DL_3_StopDate5 |  | 4x0975 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_5
| Scheduler |  |  | CO_DL_3_StopDate6 |  | 4x0976 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_6
| Scheduler |  |  | CO_DL_3_StopDate7 |  | 4x0977 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_7
| Scheduler |  |  | CO_DL_3_StopDate8 |  | 4x0978 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_8
| Scheduler |  |  | CO_DL_3_StopDate9 |  | 4x0979 |  |  |  | 0 | 34 |  | Calendar Object 3 Stop Date_9
| Scheduler |  |  | CO_DL_3_StopWeekday0 |  | 4x0980 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_0
| Scheduler |  |  | CO_DL_3_StopWeekday1 |  | 4x0981 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_1
| Scheduler |  |  | CO_DL_3_StopWeekday2 |  | 4x0982 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_2
| Scheduler |  |  | CO_DL_3_StopWeekday3 |  | 4x0983 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_3
| Scheduler |  |  | CO_DL_3_StopWeekday4 |  | 4x0984 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_4
| Scheduler |  |  | CO_DL_3_StopWeekday5 |  | 4x0985 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_5
| Scheduler |  |  | CO_DL_3_StopWeekday6 |  | 4x0986 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_6
| Scheduler |  |  | CO_DL_3_StopWeekday7 |  | 4x0987 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_7
| Scheduler |  |  | CO_DL_3_StopWeekday8 |  | 4x0988 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_8
| Scheduler |  |  | CO_DL_3_StopWeekday9 |  | 4x0989 |  |  |  | 0 | 7 |  | Calendar Object 3 Stop Weekday_9
| Scheduler |  |  | CO_DL_3_Period0 |  | 4x0990 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_0
| Scheduler |  |  | CO_DL_3_Period1 |  | 4x0991 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_1
| Scheduler |  |  | CO_DL_3_Period2 |  | 4x0992 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_2
| Scheduler |  |  | CO_DL_3_Period3 |  | 4x0993 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_3
| Scheduler |  |  | CO_DL_3_Period4 |  | 4x0994 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_4
| Scheduler |  |  | CO_DL_3_Period5 |  | 4x0995 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_5
| Scheduler |  |  | CO_DL_3_Period6 |  | 4x0996 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_6
| Scheduler |  |  | CO_DL_3_Period7 |  | 4x0997 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_7
| Scheduler |  |  | CO_DL_3_Period8 |  | 4x0998 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_8
| Scheduler |  |  | CO_DL_3_Period9 |  | 4x0999 |  |  |  | 0 | 3 |  | Calendar Object 3 Stop Period_9
| Scheduler | SO_Default |  | SO_DefaultValue |  | 4x1000 |  |  |  | 1 | 12 |  | 0-N.U., 1-Stop all, 2-Low, 3-Med, 4-High, 5-_ExtStopScheduler
© 2026 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
Note on B1: Jens B. Antonsen: Modbus and BACnet parameters reflect current values on installed components in the actual AHU. The parameters are always present, but might not be active. Actual AHU components installed depends on the AHU manufacturer brand and model.
Note on D1: Jens B. Antonsen: Standard: Always included in OJ-Air2master. Special: Partly included in some private label variants. Check the AHU controller part. No. and the AHU manufactor documentation.
Note on G1: Jens B. Antonsen: Registers start at no. 1. Adresses start at no. 0. A typical mistake is R/W to a neighbour register.
Note on K1: Jens B. Antonsen: Minimum value. Lower values will be ignored.
Note on L1: Jens B. Antonsen: Maximum value. Higher values will be ignored.
Note on M1: Jens B. Antonsen: Default valule from OJ Electronics factory.